## Slide 1: Understanding Input Harmonics and Techniques to Mitigate Them in Light of new IEEE 519-2014 Guidelines
Mahesh M. Swamy
Yaskawa America, Inc.
PP.IEEE-519.01

## Slide 2: Organization
Introduction
Why VFDs Generate Harmonics?
Harmonics and its significance in light of the new IEEE 519-2014 guidelines
Harmonic Mitigation Techniques
  Relevant and cost effective ideas to meet new guidelines
Questions and Conclusions

## Slide 3: Motivation
Harmonics cause unnecessary heat in equipment connected to harmonic source
System rich in harmonics is generally associated with poor power factor and low efficiency

## Slide 4: Motivation - Continued
Harmonics can overload preexisting power factor correcting capacitors at plant facility and at utility distribution points
Harmonics can initiate system resonance that can severely disrupt operation
Hence, control of harmonic current is important to limit voltage harmonics which can be disruptive

## Slide 5: Introduction
Non-linear loads – current does not follow applied voltage waveform

## Slide 6: Introduction (Contd.)
To estimate heating effect due to non-linear currents flowing through circuit breakers and transformers, linearization is needed
Resolving non-linear waveform into sinusoidal components is Harmonic Analysis
Ratio of harmonic content to fundamental is defined as harmonic distortion or THD

## Slide 7: Definition of THD
Ratio of the square root of the sum of squares of the rms value of harmonic component to the rms value of the fundamental component is defined as Total Harmonic Distortion (THD)

## Slide 8: Why VFDs Generate Harmonics?
Pulsating current due to dc bus capacitor – main source of non-linearity in input current
In weak ac systems, during diode conduction ac voltage is clamped to dc bus voltage – source of non-linearity in input voltage

## Slide 9: New Direction as taken by IEEE 519-2014
Voltage harmonics and system efficiency have been stressed heavily in new document
Current harmonics causes voltage harmonics – hence current harmonic control has been given due importance
System efficiency improvement has been stressed throughout the document

## Slide 10: Fundamental Shift in Focus
Voltage and Current Harmonics have been stressed to be System Specification and NOT Device Specification
Statistical Measurement has been Introduced and stressed
Utility is NOW involved in Harmonic Measurement – not the end user

## Slide 11: Fundamental Shift in Focus
* Front page of respective documents
Power Conversion Group has been completely removed!
Standard is driven by Transmission / Distribution, i.e. Producers

## Slide 12: Old Revised to New
The new document overrides the old guideline since it is noted to be a revision
Front page of respective documents

## Slide 13: Interesting Comparison Fact
IEEE 519-1992 is a 101 page document and is a “teaching or tutorial” document
In IEEE 519-2014 is only a 29 page document and there is NO attempt to educate the reader on reactive power control or harmonic current control

## Slide 14: Fundamental Shift in Focus
IEEE 519-1992: “This guide applies to all types of static power converters used in industrial and commercial power systems.”
IEEE 519-2014: “Goals for the design of electrical systems that include both linear and non linear loads are established in this recommended practice” The focus is very different as it pertains ONLY to system design and NOT to power converter equipment

## Slide 15: Point of Common Coupling
In IEEE 519-1992, point of common coupling (PCC) is vaguely defined and is open to multiple interpretations
In IEEE 519-2014, PCC is very well defined. PCC is not at the equipment but is a “Point on a Public Power Supply System”

## Slide 16: PCC Differences between 519-1992 and 519-2014
In IEEE 519-1992, point of common coupling (PCC) is also defined as follows: “Within an industrial plant, the PCC is the point between the nonlinear load and other loads.”

## Slide 17: PCC Differences between 519-1992 and 519-2014
In IEEE 519-2014, PCC is: “Frequently for service to industrial users (i.e., manufacturing plants) via a dedicated service transformer, the PCC is at the HV side of the transformer. For commercial users (office parks, shopping malls, etc.) supplied through a common service transformer, the PCC is commonly on the LV side of the service transformer.”

## Slide 18: Key Departure from the PAST
This is a Major change, if not the elimination of, the OLD and controversial way of dealing with harmonics.
“The recommended limits in this clause apply only at the point of common coupling and should not be applied to either individual pieces of equipment or at locations within a user’s facility.”
“In most cases, harmonic voltages and currents at these locations could be found to be significantly greater than the limits recommended at the PCC due to lack of diversity, cancellation, and other phenomenon that tend to reduce the combined effects of multiple harmonic sources to levels below their algebraic summation.”

## Slide 19: Total Demand Distortion - Differences between 519-1992 and 519-2014
In 519-1992, the definition of was based on the maximum load current - measurement period was 15 minutes or 30 minutes
In Section 5.2, of IEEE 519-2014, in the definition for TDD, the maximum demand current is used and is defined as:
  “This current value is established at the point of common coupling and should be taken as the sum of the currents corresponding to the maximum demand during each of the twelve previous months divided by 12”
Major shift in focus – It has shifted from short term to LONG term, stressing energy efficiency aspect of Harmonic Control

## Slide 20: System Impedance Manipulation Addressed in 519-2014
In IEEE 519-2014, system impedance manipulation by end user has been strictly curtailed. It says, “…users should not add passive equipment that affects the impedance characteristic in a way such that voltage distortions are increased.”
Explanation: Capacitors offer low impedance to harmonic currents. Flow of harmonic current into capacitors through system impedance increases system voltage distortion. Use of capacitors in filters (both active and passive) has now been restricted and the end user will be responsible if capacitor increases voltage distortion.

## Slide 21: Statistical Evaluation
Harmonic measurement will get more statistical – each frequency component packet (3-sec packet) need to be tracked for 1 day, 7 days, and 12 months!
1 day = Very Short Term; and
7 days= Short Term

## Slide 22: Harmonic Voltage Limits – IEEE 519-2014
99th percentile value (value that is exceeded for 1% of the measurement period) should be calculated for each 24-hr period for comparison with the recommended limits in Cl. 5.
95th percentile value (values that is exceeded for 5% of the measurement period) should be calculated for each 7-day period for comparison with the recommended limits in Cl. 5.
Note that there is no special or dedicated systems mentioned

## Slide 23: Current Distortion Limits – IEEE 519-2014
99th percentile value (value that is exceeded for 1% of the measurement period) should be calculated for each 24-hr period for comparison with the recommended limits in Cl. 5.
95th percentile value (values that is exceeded for 5% of the measurement period) should be calculated for each 7-day period for comparison with the recommended limits in Cl. 5.

## Slide 24: Current Distortion Limits – IEEE 519-2014

## Slide 25: Statistical Method - explained
Daily 99th percentile (value is exceeded for 1% of the measurement period of 3s) very short time harmonic currents should be less than 2.0 times the values given in Table 2.

## Slide 26: Statistical Method - explained
weekly 99th percentile (value is exceeded for 1% of the measurement period of 10 min) short time harmonic currents should be less than 1.5 times the values given in Table 2.

## Slide 27: Statistical Method - explained
weekly 95th percentile (value is exceeded for 5% of the measurement period of 10 min) short time harmonic currents should be less than 1.0 times the values given in Table 2.

## Slide 28: Recap – IEEE 519-2014
IEEE 519-2014 is a very relaxed guideline
Clearly identifies PCC and notes that measurement should NOT be performed at the device input
Stresses Long Term Averaging and strongly recommends use of Maximum Demand Current based on 12 month study
Also, for Industrial Customers, measurement is to be done on HV side of service transformer and many end users are NOT qualified to make such measurements

## Slide 29: Recap – IEEE 519-2014
Comes down hard on topologies that change the “System Impedance Characteristics” – clearly topologies that have large input capacitors should be carefully evaluated
Adding an input AC reactor or a DC link choke is perhaps the most promising and sufficient solution depending on the system
Distributing the load into phase shifted buses at the service entrance would seem to be the most cost effective way of dealing with Harmonics in Commercial and Industrial plants.

## Slide 30: Harmonic Mitigation Techniques
Active Techniques – good if used in shunt configuration for an entire subsystem or for multi drive applications
Passive Techniques – bulky and cost ineffective but certain aspects can be intelligently implemented to reduce carbon footprint

## Slide 31: Active Mitigation Techniques
Active Front End
  Boost Converter Topology – Inherently regenerative. Bulky, and expensive. Conducted EMI is of concern
Non regenerative type: Inject Current from conducting phase to non-conducting phase using semiconductor switches
Shunt type: Monitors load current and injects mirror image of load current so that harmonics cancel out.

## Slide 32: Passive Mitigation Techniques
AC Line Inductors (Reactors)
DC Link Chokes or DC Bus Inductor
Harmonic Filters – Capacitor based
Multi-pulse Schemes

## Slide 33: Passive Mitigation Techniques
AC Line Inductors (Reactors)
  Makes discontinuous current continuous
  Helps damp transient surges on line due to lightning and capacitor switching
  Small and inexpensive
  Causes voltage overlap and reduces dc bus voltage

## Slide 34: Passive Mitigation Techniques
AC Line Inductors (Reactors)
THD80%
THD40%

## Slide 35: Issues With AC Line Reactors
DC Bus Voltage Reduces Due to Overlap of Diode Conduction

## Slide 36: Passive Mitigation Techniques
DC Link Chokes (DC Bus Inductor)
  Makes discontinuous current continuous
  Small and inexpensive
  Does NOT Cause overlap phenomenon and so does not reduces dc bus voltage
  Does not help damp transient surges on line due to lightning and capacitor switching

## Slide 37: Passive Mitigation Techniques
DC Link Choke (DC Bus Inductor)
THD80%
THD37%

## Slide 38: Waveform With DC Link Choke
No overlap of Diode Conduction

## Slide 39: AC Line Reactor vs DC Link Choke

## Slide 40: AC Line Reactor vs DC Link Choke

## Slide 41: Optimal Solution
AC Line Inductor Alone Not Optimal because of Voltage Drop
DC Link Inductor Alone Does Not Provide Surge Protection
Optimal Solution is a Combination of the two – 1% AC Input Inductor + Standard DC Link Choke

## Slide 42: Issues With Capacitor based Harmonic Filters
All capacitor based shunt type filters draw leading current and cause over voltage
Capacitors offer low impedance path to harmonic currents due to pre-existing harmonic voltage in AC systems
Such deliberate harmonic current flow can cause higher voltage distortion in weak AC systems and this is often referred to as impedance manipulation
IEEE 519-2014 strictly restricts such impedance manipulation effect caused by passive components
AVOID USING CAPACITOR BASED FILTERS

## Slide 43: Multi-pulse Harmonic Mitigation Technique
12-pulse Techniques
  Three-winding isolation transformer
  Hybrid 12-pulse
  Autotransformer based 12-pulse scheme

## Slide 44: Three Winding 12-pulse Scheme
Rated for full power operation – bulky but ONLY option when input is medium voltage and drive is of low voltage rating

## Slide 45: Three Winding 12-pulse Waveforms
Load= 40hp
THD= 13.4%

## Slide 46: Hybrid 12-pulse Scheme
Transformer rated for half power – attractive option

## Slide 47: Hybrid 12-pulse Waveforms
THD= 6.7% with 5% input reactor;
8.8% with no input AC reactor.

## Slide 48: Standard Delta-Fork 12-pulse Autotransformer
12-Pulse operation not possible with above configuration since voltage across X11 and X3 is higher than X11 and X31 resulting in unequal current sharing

## Slide 49: Waveforms for 12-pulse Delta Fork Autotransformer – Not Good Performance
12 Pulse Operation is NOT possible
Stresses across Rectifier Diodes are High
DC Bus Capacitor Voltage is Higher than Normal
THD observed is 40% - close to 6-pulse performance

## Slide 50: Correct Topology For 12-pulse Autotransformer
Needs access to DC bus
Large, bulky, occupies space, and expensive
Can meet IEEE 519-2014 harmonic levels for Isc/IL > 100.

## Slide 51: 12-pulse Active Topology
Input Voltage THD= 1.48%
Input Current THD= 4.41%
True Power Factor= 0.99
Low Harmonic Distortion
Low Component Count
Needs only 0.05pu input inductor, but needs input auto transformer
Overall System Efficiency approaches 90% including motor efficiency

## Slide 52: System Approach By Employing 12-pulse Autotransformer
Good performance can be achieved by distributing loads across phase-shifted windings of autotransformer – systems approach is environmentally friendly
Cost Effective - can meet IEEE 519-2014 at PCC

## Slide 53: Typical Performance Seen on System Level Base with 12-Pulse Autotransformer Configuration
More Balanced is the Load between Outputs, better is the harmonic performance

## Slide 54: Power Factor and Harmonics
Two Definitions of Power Factor Exists
Displacement Power Factor: Cosine of the angle between the fundamental voltage and fundamental current waveform
For VFDs, this value is almost always unity (0.99)

## Slide 55: Power Factor and Harmonics
True Power Factor
  Ratio of True Power to Total Volt-Ampere Demanded by Load
  Total Volt-Ampere includes VA demanded by Harmonic Content in Waveform

## Slide 56: Power Factor and Harmonics
True Power Factor is poor:
THD80%
THD37%

## Slide 57: Conclusions
IEEE 519-2014 is a very relaxed guideline
Clearly identifies PCC and mentions it very clearly that measurement should NOT be at the device input
Stresses Long Term Averaging and strongly recommends use of Maximum Demand Current based on 12 month study
For Industrial Customers, measurement is to be done on HV side of service transformer. Many end users are NOT qualified to make such measurements

## Slide 58: Conclusions
Comes down hard on topologies that change the “System Impedance Characteristics” – clearly topologies that have large input capacitors should be carefully evaluated.
Adding an input AC reactor or a DC link choke is perhaps the most promising and sufficient solution depending on the system.
Distributing the load into phase shifted buses at the service entrance would seem to be the most cost effective way of dealing with Harmonics in Commercial and Industrial plants.

## Slide 59: Final Thoughts
“As power quality considerations evolve Yaskawa has a continued opportunity and responsibility to recommend equipment and countermeasures which both allow the customer to enjoy best value (cost) and highest system efficiency.
With the changes discussed, VFDs can be justified in more and more applications.