| Date | Customer | Job Name | P.O. / S.O. |
| --- | --- | --- | --- |

Variable Frequency Drive (VFD)

## iQpump®605 Mechanical Specification Submittal

## (For NEMA 3R / UL Type 3R Rated Bypass Drives)

# GENERAL

The iQpump605 (WM605) Bypass package provides a iQpump605 Drive in a NEMA 3R (UL Type 3R) enlosure, with a 3-contactor style bypass, allowing motor operation from either the drive or across the line. The iQpump605 features pump-specific application macros, an easy-to-read LCD keypad that provides Hand-Off-Auto interface, and a real time clock. These features make the iQpump605 perfect for most pump applications that require reliable motor control.

This drive has one control logic board and keypad for all horsepower ratings. Printed circuit boards employ surface mount technology, providing both high reliability, and small physical size of the printed circuit assemblies. The dual 32 bit microprocessors deliver the computing power necessary for complete three phase motor control in all variable-torque normal duty applications.

Operating Principle: Input three-phase AC line voltage is first rectified to a fixed DC voltage. Using pulse width modulation (PWM) inverter technology, the DC voltage is processed, to produce an output waveform in a series of variable-width pulses. Unique firmware algorithms optimize motor magnetization through control of voltage, current and frequency applied to generate a nearly sinusoidal output waveform.

# STANDARDS

UL 508C (Power Conversion)

CSA 22.2 No. 14-10 (Industrial Control Equipment)

CE mark 2006/95/EC LVD

CE mark 2004/108/EC

IEC 61800-5-1 (LVD)

EN 61800-3

IEC 60529

IEEE C62.41

UL, cUL listed; CE marked

TuV SUD

WEEE

RoHS Compliant

# BYPASS PANEL STANDARDS

UL 508A (Industrial Control Panels)

UL, cUL listed

# ENVIRONMENTAL & SERVICE CONDITIONS

Ambient service temperature: -10C to 40C (14F to 104F)

Ambient storage temperature: -20C to 60C (-4F to 140F)

Humidity: 95% RH or less, non-condensing

Altitude: Up to 1000 meters (3300 feet), higher by derating

Service factor: 1.0

Vibration:	0.33 mm Displacement (10 to 20 Hz)
	0.22 G (20 to 55 Hz)

# QUALITY ASSURANCE

In circuit testing of all printed circuit boards is conducted to ensure proper manufacturing

Final printed circuit board assemblies are functionally tested via computerized test equipment

All fully assembled controls are tested with induction motor loads to assure unit specifications are met

The average MTBF (Mean Time Between Failure) is 28 years

# DRIVE CONSTRUCTION

Input Section- The drive power input stage converts three-phase AC line power into a fixed DC voltage via a solid-state full wave diode rectifier with MOV (Metal Oxide Varistor) surge protection. An internal 3% DC bus reactor at ratings of greater than 30HP reduces harmonics (optional at smaller ratings).

Intermediate Section- The DC bus maintains a fixed, filtered DC voltage with short circuit protection as a DC supply for the drive output section. The DC bus is monitored by drive diagnostic logic circuits to continuously protect and monitor the power components.

Output Section- Insulated Gate Bipolar Transistors (IGBTs) convert DC bus voltage to a variable frequency, variable voltage PWM sine-coded AC output to the motor.  Use of IGBT devices allow motor noise at 60 Hz to measure less than 2 dB (@ 1 meter) above that resulting from across the line operation.

Available horsepower ratings:

208VAC: 1 thru 100 HP
240VAC: 1 thru 100 HP
480VAC: 1 thru 250 HP

Microprocessor based control circuit uses non-volatile memory (NVRAM) so all programming data is saved when the drive is disconnected from power

Current transformers detect the output current for motor control and protective functions

Multi-language 5-line 16-character LCD Hand-Off-Auto keypad with real time clock. Provides local programming, run/stop control, monitoring, speed reference and reset commands

Customizable display of readouts including output frequency, output voltage, output current, output power, DC bus voltage, PI feedback and fault status. Includes parameter settings copy backup function

Built-In real time clock for time/date stamping of fault events along with timer functions for starting, stopping and speed changes without the need for external controls

Removable I/O terminal board has backup memory. All parameter changes are automatically saved to both the main control board and the I/O board. Leave I/O wiring connected when replacing a drive

Easy to remove DC voltage heat sink cooling fans with programmable on/off control

USB Type B port for quick and easy PC Connection

# PROTECTION

Output current overload rating: 110% of drive’s continuous current rating for 60 seconds

Output short circuit protection

Current limited stall prevention (overload trip prevention) during acceleration, deceleration, and run conditions

Optically isolated operator keypad controls

Fault display with time stamp storage of last 10 faults

Motor hunting prevention function

Electronic ground fault protection

Electronic thermal motor overload (UL approved) protects the motor while operating in drive and bypass mode

Motor current displays in both drive and bypass modes of operation as well as verification that the motor is running

Proof of flow/loss of flow detection in both drive and bypass modes

DC bus charge indication

Heat sink over temperature protection

Cooling fan operation hours monitor

Input/output phase loss protection

Line voltage sensors to monitor for brownout and blackout conditions with adjustable fault levels to ensure the proper settings pursuant to each application.

Reverse prohibit function

Short circuit withstand rating of 65kAIC RMS, 100kAIC RMS with optional breaker

# OPERATION

Over 100 programmable functions with resettable factory pump presets

User parameter settings initialization for re-establishing project specific parameter settings

Output frequency and speed display can be programmed for speed-related and control indications including: Hz, RPM, % or custom units

Power loss ride-thru (2 seconds capable)

Time delay on start, peak avoidance

Drive accepts either a direct acting or a reverse acting speed command signal

Bi-directional speed search capability allows starting into a rotating load. Two types: current detection and residual voltage detection

Ramp-to-stop or coast-to-stop selection

Auto restart capability: 0 to 10 attempts with adjustable delay time between attempts

One custom selectable Volts/Hertz pattern and multiple preset Volts/Hertz patterns

Analog speed reference signals have adjustable bias and gain

Automatic energy savings, reduced voltage operation

While the drive is running, operational changes in control and display functions are possible including:

Hand/Off/Auto commands
	Start/stop commands
	Frequency reference command
	Acceleration time (0 to 6000 seconds)
	Deceleration time (0 to 6000 seconds)
	Monitor displays
	Remove the operator keypad

# PRODUCT FEATURES

Displacement power factor: 0.98 throughout the motor speed range

Drive efficiency: 96% at half-speed; 98% at full-speed

Starting torque capability: 150% from 3 Hz

Speed control range: 40:1

Carrier frequency: adjustable from 1 kHz to 15 kHz

Input phase insensitive; sequencing of the three phase input is unnecessary

Voltmeter, ammeter, kilowatt meter, elapsed run time meter and heatsink temperature monitoring functions

Two internal (PI) Controls:

- Drive internal PI closed loop control with selectable engineering units

- Independent PI control of external devices

Differential PI feedback feature

Sleep function in both closed loop and open loop control

Feedback signal low pass filter

Optional network communications include:

EtherNet/IP

EtherNet/IP dual port

Modbus/TCP

Modbus/TCP dual port

BACnet MSTP

APOGEE/METASYS

Self-regulating lead/lag control for multiple drives (up to 5 pumps)

Drive/motor alternation control (share motor run time for lead drive/motor)

Up to four PID setpoints

Enhance pump control features:

Easy sleep/wakeup PID setup

No flow/deadhead protection

Submersible motor thrust bearing control

Automatic system restart

Sleep boost

Low and high pressure feedback detection

Power loss utility start delay timer

Loss of prime (LOP)/pump dry-run protection

Pre-charge control (controlled pipe fill)

Optional dual transducer feedback for redundancy

Impeller de-scaling/de-ragging control

Low city, low/high water alarm digital input selections

Draw down start level selection for PID setpoint

Contactor Multiplexing features:

Stage/de-stage control – add/remove drive based on feedback or output frequency

Speed reduction after lag pump staging

Setpoint boost after de-staging

Hard current limit

Back spin timer

Feedback signal loss detection with selectable response

Feedback signal inverse capability

Feedback transmitter power supply: 24 VDC, 150 mA

Input and output terminal status monitors

Diagnostic fault/alarm indicators with dedicated contacts

S-curve soft start / soft stop capability

Network communication loss detection with selectable response

Up/down motor operated pot (MOP) floating point control

17 preset speeds

Critical frequency rejection capability: 3 selectable, adjustable bandwidths

Dynamic noise control function for quiet motor operation

Programmable security code for operator keypad lockout

Run/stop command methods:

Terminal strip (2-wire or 3-wire)
	Network communication
	Operator keypad

Speed reference (speed command) methods:

0 to 10 VDC or -10 to 10 VDC (20 k)
	4 to 20 mA or 0 to 20 mA (250 )
	0 to 32 kHz pulse train
	Network communication
	Operator keypad

Eight programmable multi-function digital input terminals (24 VDC, sinking or sourcing, internal/external power supply) providing 60+ programmable functions including:

Multi-step speed references
	Jog commands
	PID control enable/disable

Three programmable multi-function digital output terminals (2 Form-A and 1 Form-C relays, 1 A @ 250 VAC / 30 VDC) providing 50+ functions including:

During run
	Drive ready
	Speed agree
	No load detection (broken belt/shaft alert)

One fixed Fault output relay (Form-C, 1 A @ 250 VAC / 30 VDC)

Three programmable multi-function analog input terminals (individually selectable for 0 to 10 VDC, -10 to 10 VDC, 4 to 20 mA, or 0 to 20 mA) providing 15+ functions including:

Frequency reference
	PID setpoint
	PID feedback

Two programmable multi-function analog output terminals (individually selectable for 0 to 10 VDC, -10 to 10 VDC, or 4 to 20 mA) providing 20+ functions including:

Output Frequency
	Output Current
	Output Power

One programmable multi-function pulse train input terminal (0 to 32 kHz) providing several functions including:

Frequency reference
	PID setpoint
	PID feedback

1 fixed Fault output relay (Form-C, 1 A @ 250 VDC / 30 VDC)

1 built-in RS-485, 115.2 kbps Modbus/Memobus network communication port

Stationary and rotational motor auto-tuning

Overexcitation braking function stops the motor in up to half the normal time

Motor preheat function

Upgradeable drive firmware via PC program

Heat sink over temperature speed fold-back feature

Bumpless transfer between local and remote modes

# BYPASS FEATURES

Bypass and drive are factory assembledBypass and Drive input/output contactors

Lockable Main Input circuit breaker (65kAIC panel rating)

Thermal motor overload relay, class 20

115 VAC control transformer, fused

Drive H/O/A keypad used for bypass control

Selectable energy savings and harmonic reduction mode.

No load detection (loss of load) fully monitored in drive and bypass modes

Door mounted control keypad with LCD display for “Control Power”, “Drive Ready”, “Drive Run”, “Drive Selected”,  “Drive Fault”, “Drive Test”,  “Bypass Selected”,  “Bypass Run”, “Motor OL”, ”Safety Open” “BAS Interlock”, “Auto Run”, Auto Transfer”, “Hand Mode”, “Off Mode”, and “Auto Mode”

7 programmable multi-function digital input terminals (24 VDC, 8 mA) providing 60+ programmable functions including:

Customer Safeties
	Preset Speed
	PI control enable / disable

4 programmable multi-function digital output terminals (Form-C relays, 2 A @ 120 VAC / 24 VDC) providing 50+ functions including:

Hand / Auto Status
	Contactor Control for External Bypass
	Overtorque/undertorque detection

Auto speed reference (speed command) methods:

0 to 10 VDC (20 k)
	4 to 20 mA (250 )

Model Number Configuration

Step 1. Complete the Base Number for the voltage and current.

Step 2. Add the Option Code letter for each required option. If an option is not wanted, no character is inserted at that position.

ENCLOSURE TYPE

[3] NEMA 3R (UL Type 3R) Enclosure

VOLTAGE

[D] 208 volt models, 200 to 240 VAC (+10/-15 %); 50/60 Hz (+/-5%)

[A] 240 volt models, 200 to 240 VAC (+10/-15 %); 50/60 Hz (+/-5%)

[B] 480 volt models, 380 to 480 VAC (+10/-15 %); 50/60 Hz (+/-5%)

[P] POWER OPTIONS

MAIN INPUT DISCONNECT (Choose None or One)

[E] Circuit Breaker Disconnect (Standard AIC)

[C] Circuit Breaker Disconnect (High AIC)

ADDITIONAL POWER OPTIONS (Choose None or One)

[G] Drive Input Disconnect Switch

[B] 3-Contactor Bypass

REACTOR (Choose None or One)

[R] 3% Line Reactor

[H] 3% Load Reactor

ADDITIONAL POWER OPTIONS (Choose None or One)

[2] Surge Arrestor, Low Capacity

[7] Raycap Surge Arrestor

[9] Raycap Surge Arrestor (277 Delta-Wye)

ADDITIONAL POWER OPTIONS (Choose None or One)

[3] Space Heater

ADDITIONAL POWER OPTIONS (Choose None or One)

[4] 50°C Ambient

[T] CONTROL OPTIONS

[W] Custom Nameplates

NETWORK COMMUNICATION (Choose None or One)

[3] Multi-protocol Ethernet (Dual Port)

[H] PROFIBUS

[J] BACnet MSTP

[L] LonWorks

I/O OPTION CARD (Choose None or One)

[E] Digital Output

[N] Analog Output

CONTROL OPTIONS (Choose None or One)

[6] Start/Stop PBs

[9] Speed Pot/HOA SS

ADDITIONAL CONTROL OPTIONS (Choose None, Any, or All)

[6] Start/Stop PBs

[9] Speed Pot/HOA SS

ADDITIONAL CONTROL OPTION (Choose None or One)

[M] Keypad Viewing Window

SPECIAL OPTIONS

[B] Bluetooth Keypad

Tag:

Model Number:

HP:

Amps:

Volts: