## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  | A.C. LINE WIRING
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | WITH OPTION PM CIRCUIT BREAKER CB1 | [5 empty] | STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1
208V | 480V | MFG. PART NUMBER |  | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) |  | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER |  | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) |  | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | H_ _36015 |  | 15 | 14 - 10 OR 8 - 3/0 |  | 50 OR 120 | V0 |  | 20 | 14 - 8 |  | 19
D003 | B002
D004 | B003
B004
D006 | B007 | H_ _36020 |  | 20
D007
D010 | B011 | H_ _36025 |  | 25
| B014 | H_ _36035 |  | 35
D016 |  | H_ _36040 |  | 40
| B021 | H_ _36050 |  | 50 |  |  |  | V3 |  | 45 | 12 - 6 |  | 40
D024 | B027 | H_ _36060 |  | 60
D030 | B034 | H_ _36070 |  | 70 |  |  |  | V4 |  | 63 | 6 - 2 |  | 50
| B040 | H_ _36080 |  | 80
D046 | B52L | H_ _36110 |  | 110 |  |  |  | V5 |  | 100 | 8 - 2/0 |  | 200
B052
D059 |  | H_ _36125 |  | 125
| B065 | H_ _36150 |  | 150
| B077 | [6 empty] | H_ _36000S15 |  | 150 | 8 - 3/0 |  | 120
B096
D074 | [7 empty] | V6 |  | 115 | 8 - 2/0 |  | 200
D088 | [7 empty] | H_ _36000S15 |  | 150 | 8 - 3/0 |  | 120
D114 | [7 empty] | J_ _36000S17 |  | 175 | 4 - 4/0 |  | 225
| B124 | J_ _36250 |  | 250 | 4 - 4/0 |  | 225
D143 | B156 |  |  |  | 3/0 - 350 kcmil |  | 225 | J_ _36000S25 |  | 250 | 3/0 - 350 kcmil |  | 225
D169 | B180
D211 |  | L_ _36400U31X |  | 400 | (1-2) x (2/0 - 500 kcmil) |  | (1-2) x 442 | L_ _36000S40X |  | 400 | (1-2) x (2/0 - 500 kcmil) |  | (1-2) x 442
D273 | B240 | L_ _36600U31X |  | 600
| B302 | [6 empty] | L_ _36000S60X |  | 600
D343 | B361 | P_ _34060 |  | 600 | (1-3) x (3/0 - 500 kcmil) |  | (1-3) x 450
D396 | B414
| B477 | P_ _34080 |  | 800 |  |  |  | P_ _34000S80 |  | 800 | (1-3) x (3/0 - 500 kcmil) |  | (1-3) x 450
B515
| B590 | [6 empty] | P_ _34000S10 |  | 1000 | (1-4) x (3/0 - 500 kcmil) |  | (1-4) x 450
TABLE 2 |  | A.C. MOTOR WIRING | [8 empty] | EARTH GROUND WIRING |  | CONTROL WIRING
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | STANDARD BYPASS MOTOR OVERLOAD RELAY |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUG |  | A1 TERMINAL BLOCKS TB1-TB4 AND PANEL MOUNTED TERMINAL BLOCK TB1 |  | A2 TERMINAL BLOCKS TB1-TB3
208V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | LRD06 | 18 - 8 | 15 | LRD05 | 18 - 8 | 15 | LC1D09 | 18 - 10 | 15 | 14 - 10 | 35 | 24 - 16 | 4.4 - 5.3 | 26 - 12 | 4
D002 | B002 | LRD07 |  |  | LRD06
D003 | B003 | LRD15 |  |  | LRD07
D004 | B004 | [9 empty] | OR | OR
D006 | B007 |  |  |  | LRD1508
D007
D010 | B011 |  |  |  | LRD1510 | [5 empty] | 8 | 40
| B014 |  |  |  | LRD1512 |  |  | LC1D18 | 18 - 8
D016 |  |  |  |  | LRD1514
D024 | B021 |  |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20
D030 | B027 |  |  |  | LRD1521 |  |  | LC1D32 |  |  | OR | OR
| B034 | LRD340L | 16 - 2 | 70 |  |  |  | LC1D40 | 16 - 2 | 70
| B040 |  |  |  | LRD1522
D046 |  | LRD350L | [5 empty] | LC1D50
D059 | B52L | LRD365L |  |  | LRD1532 | [5 empty] | 6 - 4 | 45
B052
| B065 | LR2 D35 | 10 - 1/0 | 100 | LRD340L | 16 - 2 | 70 | LC1D65
D074 | B077 | [6 empty] | LC1D80 | 10 - 2 | 100
D088 | B096 | LR9-F5567 | 6 - 3/0 | 200 | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil |  | OR | OR
D114 | B124 | LR9-F5569 |  |  | LRD365L
D143 |  |  |  |  | LR2D3563 | 10 - 1/0 | 100
D169 | B156 | LR9-F5571 | 6 - 300 kcmil | 275 | LR9-F5567 | 6 - 3/0 | 200
| B180 | [9 empty] | 2 | 50
D211 | B240 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | LR9-F5569 |  |  | LC1F500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | 14 - 2/0 | 120
D273
| B302 | LR9-F7579 |  |  | LR9-F5571 | 6 - 300 kcmil | 275
D343 | B361 | LR9G500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D396 | B414
| B477 | LR9G630 | (1-3) x (2 - 600 kcmil) | (1-3) x 500 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 |  |  |  | 6-250 kcmil | 275
B515
B590
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[17 empty] | Rev | Description | ECO# | Drawn By | Date
[17 empty] | 06 | CHG. OVERLOAD RELAY FOR STANDARD BYPASS D343,396 AND B361,414,477,515,590 MODELS | 15062 | KM | 2026-02-03
[17 empty] | 05 | ADDED "USE COPPER CONDUCTORS ONLY" TO CUST. WIRING REQUIREMENTS | 7469 | KM | 2016-10-27
[17 empty] | 04 | ADDED B52L | 5024 | AIM | 2014-02-19
ECO #
DRAWN BY
DATE
DESCRIPTION
CHG. OVERLOAD RELAY FOR STANDARD BYPASS D343,396 AND B361,414,477,515,590 MODELS
ADDED "USE COPPER CONDUCTORS ONLY" TO CUST. WIRING REQUIREMENTS
ADDED B52L
REV.
06
05
04
15062
7469
5024
KM
KM
AIM
02/03/26
10/27/16
02/19/14
REVISIONS
TITLE:
CUSTOMER CONNECTION
Z1000 BYPASS
SIZE:
C
PAGE:
1 of 1
REVISION:
06
DRAWING #:
UDE00349
DRAWN BY:
D. PACKER
CHECKED:
D.R. CMELAK
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
K. MALUSIC
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
01/23/13
DATE:
01/23/13
DATE:
DATE:
01/23/13
DATE:
10/17/11