## Sheet1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE.
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE.
TABLE 1 |  | A.C. LINE WIRING | [5 empty] | CONTROL WIRING
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | CIRCUIT BREAKER CB1 | [5 empty] | A1 TERMINAL BLOCKS TB1-TB4 |  | A2 TERMINAL BLOCKS TB1-TB3 |  | PANEL TERMINAL BLOCK TB1
208V | 480V | MFG. PART NUMBER |  | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) |  | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | H_ _36015 |  | 15 | 14 - 10 OR 8 - 3/0 |  | 50 OR 120 | 24 - 16 | 4.4 - 5.3 | 26 - 12 | 4 | 24 - 16 | 4.4 - 5.3
D003 | B002
D004 | B003
B004
D006 | B007 | H_ _36020 |  | 20
D007 |  | H_ _36025 |  | 25
D010 | B011
| B014 | H_ _36035 |  | 35
D016 |  | H_ _36040 |  | 40
| B021 | H_ _36050 |  | 50
D024 | B027 | H_ _36060 |  | 60
D030 | B034 | H_ _36070 |  | 70
| B040 | H_ _36080 |  | 80
D046 | B052 | H_ _36110 |  | 110
D059 |  | H_ _36125 |  | 125
| B065 | H_ _36150 |  | 150
B077
B096
D074
D088
D114
| B124 | J_ _36250 |  | 250 | 4 - 4/0 |  | 225
D143 | B156 |  |  |  | 3/0 - 350 kcmil |  | 225
D169 | B180
D211 |  | L_ _36400U31X |  | 400 | (1-2) x (2/0 - 500 kcmil) |  | (1-2) x 442
D273 | B240 | L_ _36600U31X |  | 600
B302
D343 | B361 | P_ _34060 |  | 600 | (1-3) x (3/0 - 500 kcmil) |  | (1-3) x 450
D396 | B414
| B477 | P_ _34080 |  | 800
B515
B590
TABLE 2 |  | A.C. MOTOR WIRING | [8 empty] | EARTH GROUND WIRING |  | NEUTRAL
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | STANDARD BYPASS MOTOR OVERLOAD RELAY |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUGS |  | TERMINAL BLOCK TBN1
208V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | LRD06 | 18 - 8 | 15 | LRD05 | 18 - 8 | 15 | LC1D09 | 18 - 10 | 15 | 14 - 10 | 35 | 16 - 10 | 35
D002 | B002 | LRD07 |  |  | LRD06 | [5 empty] | OR | OR | OR | OR
D003 | B003 | LRD15 |  |  | LRD07 | [5 empty] | 8 | 40 | 8 | 40
D004 | B004 | [9 empty] | OR | OR | OR | OR
D006 | B007 |  |  |  | LRD1508 | [5 empty] | 6 - 4 | 45 | 6 - 4 | 45
D007 | [10 empty] | OR | OR
D010 | B011 |  |  |  | LRD1510 | [5 empty] | 2 - 1/0 | 50
| B014 |  |  |  | LRD1512 |  |  | LC1D18 | 18 - 8
D016 |  |  |  |  | LRD1514
D024 | B021 |  |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20
D030 | B027 |  |  |  | LRD1521 |  |  | LC1D32
| B034 | LRD340L | 16 - 2 | 70 |  |  |  | LC1D40 | 16 - 2 | 70 | 14 - 2/0 | 120 | 14 - 10 | 35
| B040 |  |  |  | LRD1522 | [7 empty] | OR | OR
D046 |  | LRD350L | [5 empty] | LC1D50 |  |  |  |  | 8 | 40
D059 | B052 | LRD365L |  |  | LRD1532 | [7 empty] | OR | OR
| B065 | LR2 D35 | 10 - 1/0 | 100 | LRD340L | 16 - 2 | 70 | LC1D65 |  |  |  |  | 6 - 2/0 | 120
D074 | B077 | [6 empty] | LC1D80 | 10 - 2 | 100
D088 | B096 | LR9-F5567 | 6 - 3/0 | 200 | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil
D114 | B124 | LR9-F5569 |  |  | LRD365L
D143 |  |  |  |  | LR2D3563 | 10 - 1/0 | 100 |  |  |  | (1-2) x (6 - 250 kcmil) | (1-2) x 275 | 6 - 350 kcmil | 275
D169 | B156 | LR9-F5571 | 6 - 300 kcmil | 275 | LR9-F5567 | 6 - 3/0 | 200
B180
D211 | B240 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | LR9-F5569 |  |  | LC1F500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D273
D343 | B302 | LR9-F7579 |  |  | LR9-F5571 | 6 - 300 kcmil | 275
D396 | B361
| B414 | LR9-F7581 | (1-3) x (2 - 600 kcmil) | (1-3) x 500
| B477 |  |  |  | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
B515
B590
TITLE:
CUSTOMER CONNECTION
Z1000 BYPASS
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00423
DRAWN BY:
D.R. CMELAK
CHECKED:
K. MALUSIC
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
D.R. CMELAK
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
04/30/13
DATE:
04/30/13
DATE:
DATE:
04/30/13
DATE:
04/30/13
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
DRC
4/30/13
REVISIONS