## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  | A.C. LINE WIRING | [5 empty] | CONTROL WIRING
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | CIRCUIT BREAKER CB1 | [5 empty] | A1 TERMINAL BLOCKS TB1-TB4 |  | A2 TERMINAL BLOCKS TB1-TB3 |  | PANEL TERMINAL BLOCK TB1
208V | 480V | MFG. PART NUMBER |  | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) |  | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | H_ _36015 |  | 15 | 14 - 10 OR 8 - 3/0 |  | 50 OR 120 | 24 - 16 | 4.4 - 5.3 | 26 - 12 | 4 | 24 - 16 | 4.4 - 5.3
D003 | B002
D004 | B003
B004
D006 | B007 | H_ _36020 |  | 20
D007
D010 | B011 | H_ _36025 |  | 25
| B014 | H_ _36035 |  | 35
D016 |  | H_ _36040 |  | 40
| B021 | H_ _36050 |  | 50
D024 | B027 | H_ _36060 |  | 60
D030 | B034 | H_ _36070 |  | 70
| B040 | H_ _36080 |  | 80
D046 | B52L | H_ _36110 |  | 110
B052
D059 |  | H_ _36125 |  | 125
| B065 | H_ _36150 |  | 150
B077
D074
D088
D114 | B096 | J_ _36250 |  | 250 | 4 - 4/0 |  | 225
B124
D143 | B156 |  |  |  | 3/0 - 350 kcmil |  | 225
D169 | B180 | L_ _36400U31X |  | 400 | (1-2) x (2/0 - 500 kcmil) |  | (1-2) x 442
D211
D273 | B240 | L_ _36600U31X |  | 600
B302
D343 | B361 | P_ _34060 |  | 600 | (1-3) x (3/0 - 500 kcmil) |  | (1-3) x 450
D396 | B414
| B477 | P_ _34080 |  | 800
B515
B590
TABLE 2 |  | A.C. MOTOR WIRING | [8 empty] | EARTH GROUND WIRING |  | NEUTRAL
Z1000 BYPASS MODEL NO. BASE NUMBER Z1B_XXXX |  | STANDARD BYPASS MOTOR OVERLOAD RELAY |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUGS |  | TERMINAL BLOCK TBN1
208V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | LRD06 | 18 - 8 | 15 | LRD05 | 18 - 8 | 15 | LC1D09 | 18 - 10 | 15 | 14 - 10 | 35 | 14 - 10 | 35
D002 | B002 | LRD07 |  |  | LRD06 | [5 empty] | OR | OR | OR | OR
D003 | B003 | LRD15 |  |  | LRD07 | [5 empty] | 8 | 40 | 8 | 40
D004 | B004 | [9 empty] | OR | OR | OR | OR
D006 | B007 |  |  |  | LRD1508 | [5 empty] | 6 - 4 | 45 | 6 - 4 | 45
D007 | [10 empty] | OR | OR | OR | OR
D010 | B011 |  |  |  | LRD1510 | [5 empty] | 2 - 1/0 | 50 | 2 | 50
| B014 |  |  |  | LRD1512 |  |  | LC1D18 | 18 - 8
D016 |  |  |  |  | LRD1514
D024 | B021 |  |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20
D030 | B027 |  |  |  | LRD1521 |  |  | LC1D32 |  |  | 14 - 2/0 | 120 | 14 - 10 | 35
| B034 | LRD340L | 16 - 2 | 70 |  |  |  | LC1D40 | 16 - 2 | 70 |  |  | OR | OR
| B040 |  |  |  | LRD1522 | [7 empty] | 8 | 40
D046 |  | LRD350L | [5 empty] | LC1D50 |  |  |  |  | OR | OR
D059 | B52L | LRD365L |  |  | LRD1532 | [7 empty] | 6 - 2/0 | 120
B052
| B065 | LR2 D35 | 10 - 1/0 | 100 | LRD340L | 16 - 2 | 70 | LC1D65
D074 | B077 | [6 empty] | LC1D80 | 10 - 2 | 100
D088 |  | LR9-F5567 | 6 - 3/0 | 200 | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil
| B096 | LR9-F5567 |  |  | LRD350L | [5 empty] | (1-2) x (6 - 250 kcmil) | (1-2) x 275 | 6 - 350 kcmil | 275
D114 | B124 | LR9-F5569 |  |  | LRD365L
D143 |  |  |  |  | LR2D3563 | 10 - 1/0 | 100
| B156 | LR9-F5571 | 6 - 300 kcmil | 275 | LR9-F5567 | 6 - 3/0 | 200 | LC1D150
D169 | B180 | [6 empty] | LC1F265 | 6 - 350 kcmil | 275
D211 | B240 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | LR9-F5569 |  |  | LC1F330 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D273
| B302 | LR9-F7579 |  |  | LR9-F5571 | 6 - 300 kcmil | 275 | LC1F400
D343 | B361 | LR9G500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D396 | B414
| B477 | LR9G630 | (1-3) x (2 - 600 kcmil) | (1-3) x 500 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | LC1F500
B515
B590
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[15 empty] | Rev | Description | ECO# | Drawn By | Date
[15 empty] | 05 | CHG. OVERLOAD RELAY FOR STANDARD BYPASS D343,396 AND B361,414,477,515,590 MODELS | 15062 | KM | 2026-02-03
[15 empty] | 04 | UPDATE INPUT/OUTPUT TERMINAL BLOCK | 12994 | JZ | 2023-04-10
[15 empty] | 03 | ADDED "(USE COPPER CONDUCTORS ONLY)" TO CUST. WIRING REQ. | 7469 | KM | 2016-11-10
ECO #
DRAWN BY
DATE
DESCRIPTION
CHG. OVERLOAD RELAY FOR STANDARD BYPASS D343,396 AND B361,414,477,515,590 MODELS
UPDATE INPUT/OUTPUT TERMINAL BLOCK
ADDED "(USE COPPER CONDUCTORS ONLY)" TO CUST. WIRING REQ.
REV.
05
04
03
15062
12994
7469
KM
JZ
KM
02/03/26
04/10/23
11/10/16
REVISIONS
TITLE:
CUSTOMER CONNECTION
Z1000 BYPASS
SIZE:
C
PAGE:
1 of 1
REVISION:
05
DRAWING #:
UDE00424
DRAWN BY:
D.R. CMELAK
CHECKED:
K. MALUSIC
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
D.R. CMELAK
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
04/30/13
DATE:
04/30/13
DATE:
DATE:
04/30/13
DATE:
04/30/13