## UDE00426_R00
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE.
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE.
TABLE 1 |  | A.C. LINE WIRING | [7 empty] | CONTROL WIRING
Z1000 CONFIGURED MODEL NO. BASE NUMBER Z1C_XXXX |  | WITH OPTION PC OR PM CIRCUIT BREAKER CB1 |  |  |  | STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1 |  |  |  | A1 TERMINAL BLOCKS TB1-TB4 AND PANEL MOUNTED TERMINAL BLOCK TB1 |  | A1 TERMINAL BLOCK TB5 (FE)
208V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | V0 | 20 | 14 - 8 | 19 | 24 - 16 | 4.4 - 5.3 | 14 - 22 | 4.4 - 5.3
D003 | B002
D004 | B003
D006 | B004
D007 | B007
D010 | B011 | H_ _36020 | 20
| B014 | H_ _36025 | 25
D016 |  | H_ _36030 | 30 |  |  | V3 | 45 | 12 - 6 OR 6 - 2 | 40 OR 50
| B021 | H_ _36035 | 35
D024 |  | H_ _36040 | 40
| B027 | H_ _36045 | 45
D030 | B034 | H_ _36050 | 50 |  |  | V4 | 63
| B040 | H_ _36060 | 60
D046 |  | H_ _36070 | 70 |  |  | V5 | 100 | 8 - 2/0 | 200
| B052 | H_ _36080 | 80
D059 | B065 | H_ _36100 | 100
D074 | B077 | H_ _36110 | 110
| B096 | H_ _36150 | 150 |  |  | V6 | 115
D088 | [5 empty] | H_ _36000S15 | 150 | 8 - 3/0 | 120
D114 | B124 | J_ _36175 | 175 | 4 - 4/0 | 225 | J_ _36000S17 | 175 | 4 - 4/0 | 225
D143 | B156 | J_ _36250 | 250 | 3/0 - 350 kcmil | 225 | J_ _36000S25 | 250 | 3/0 - 350 kcmil
D169 | B180
D211 | B240 | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442 | L_ _36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D273
| B302 |  |  |  |  | L_ _36000S60X | 600
D343 | B361 | L_ _36600U31X | 600
D396 | B414
| B477 | P_ _3_080 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | P_ _34000S80 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
B515
B590
TABLE 2 |  | A.C. MOTOR WIRING | [9 empty] | EARTH GROUND WIRING
Z1000 CONFIGURED MODEL NO. BASE NUMBER Z1C_XXXX |  | WITHOUT OPTION PK, PA, OR PY TO STANDARD AC DRIVE | OR, WITH OPTION PK LOAD REACTOR L4 |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUG
208V | 480V |  | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75°C COPPER WIRE ONLY | RLW-02P10_ | 22 - 10 | 4.5 | LRD05 | 18 - 8 | 15 | LC1D09 | 18- 10 | 15 | 14 -10 | 35
D002 | B002 |  | RLW-03P40_ |  |  | LRD06
D003 | B003 |  | RLW-04P80_ |  |  | LRD07
D004 | B004 |  | RLW-07P60_
D006 | B007 |  | RLW-00110_ |  |  | LRD1508 | [5 empty] | OR | OR
D007
D010 | B011 |  | RLW-00140_ |  |  | LRD1510
| B014 |  | RLW-00210_ | 14 - 6 | 16 | LRD1512 |  |  | LC1D18 | 18 - 8 |  | 8 | 40
D016 | [5 empty] | LRD1514
| B021 |  | RLW-00280_ |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20
D024 |  |  | RLW-00350_
| B027 |  |  |  |  | LRD1521 |  |  | LC1D32 |  |  | OR | OR
D030 |  |  | RLW-00460_
| B034 | [7 empty] | LC1D40A | 16 - 2 | 70
| B040 |  | RLW-00550_ | 6 - 1/0 | 45 | LRD1522 | [5 empty] | 6 - 4 | 45
D046 |  |  | RLW-00650_ | [5 empty] | LC1D50A
| B052 |  |  |  |  | LRD1532
D059 |  |  | RLW-00830_ |  |  | LRD1532
| B065 |  |  |  |  | LRD340L | 16 - 2 | 70 | LC1D65A |  |  | OR | OR
D074 | B077 |  | RLW-01040_ | [5 empty] | LC1D80 | 10 - 2 | 100
D088 | B096 |  | RLW-01300_ | 2 - 1 OR 1/0 - 2/0 OR 3/0 - 4/0 | 150 OR 180 OR 250 | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil
D114 | B124 |  | RLW-01600_ |  |  | LRD365L | [5 empty] | 2 | 50
D143 |  |  | RLW-02000_ |  |  | LR2D3563 | 10 - 1/0 | 100 |  |  |  | 14 - 2/0 | 120
| B156 |  |  |  |  | LR9-F5567 | 6 - 3/0 | 200
D169 | B180 |  | RLW-02500_ | 250 - 350 kcmil | 325
D211 | B240 |  | RLW-03220_ |  |  | LR9-F5569 |  |  | LC1F500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D273 |  |  | RLW-04140_ | (1 - 2) x (6 - 350 kcmil) | (1 - 2) x (375)
| B302 |  |  |  |  | LR9-F5571 | 6 - 300 kcmil | 275
D343 | B361 |  | RLW-05150_
D396 | B414 |  | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR
| B477 |  |  |  |  | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 |  |  |  | 6 - 250 kcmil | 275
| B515 |  | RLW-07500_
B590
TITLE:
CUSTOMER CONNECTION
Z1000 CONFIGURED
TYPE 12
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00426
DRAWN BY:
D. PACKER
CHECKED:
D. CMELAK
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
D. PACKER
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
06/08/13
DATE:
06/08/13
DATE:
DATE:
06/08/13
DATE:
06/08/13
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
DJP
6/08/13
REVISIONS