## Sheet1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE.
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE.
TABLE 1 |  | A.C. LINE WIRING | [7 empty] | CONTROL WIRING
Z1000 CONFIG. MODEL NO. BASE NUMBER Z1C_XXXX |  | WITH OPTIONS PC OR PM CIRCUIT BREAKER CB1 |  |  |  | OR, STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1 |  |  |  | A1 TERMINAL BLOCKS TB1-TB4 |  | A1 TERMINAL BLOCK TB5 (FE) |  | PANEL TERMINAL BLOCK TB1
208V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | H__36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | 24 - 16 | 4.4 - 5.3 | 22 - 14 | 4.4 - 5.3 | 24 - 16 | 4.4 - 5.3
D002 | B002
D003 | B003
D004 | B004
D006 | B007 | H_ _36020 | 20
D007
D010 | B011 | H_ _36025 | 25
| B014 | H_ _36030 | 30
D016 |  | H_ _36035 | 35
| B021 | H_ _36040 | 40
D024 |  | H_ _36045 | 45
| B027 | H_ _36050 | 50
D030 | B034 | H_ _36060 | 60
| B040 | H_ _36070 | 70
D046 | B052 | H_ _36080 | 80
D059 |  | H_ _36100 | 100
| B065 | H_ _36110 | 110
D074 | B077 | H_ _36125 | 125
D088 |  | H_ _36150 | 150
| B096 | J_ _36175 | 175 | 4 - 4/0 | 225
D114 |  | J__36200 | 200
| B124 |  |  |  |  | J__36000S17 | 175 | 4 - 4/0 | 225
D143 | B156 | J__36250 | 250 | 3/0 - 350 kcmil | 225 | J__36000S25 | 250 | 3/0 - 350 kcmil | 225
D169
| B180 | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D211 | B240 |  |  |  |  | L__36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D273 | B302
D343 |  | L_ _36600U31X | 600 |  |  | L__36000S60X | 600
D396 | B361
B414
| B477 | P_ _3_080 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | P__34000S80 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
B515
B590
TABLE 2 |  | A.C. MOTOR WIRING | [9 empty] | EARTH GROUND WIRING |  | NEUTRAL
Z1000 CONFIG. MODEL NO. BASE NUMBER Z1C_XXXX |  | WITHOUT OPTIONS PK, PA OR PY TO STANDARD AC DRIVE | OR, WITH OPTION PK LOAD REACTOR L4 |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUGS |  | TERMINAL BLOCK TBN1
208V | 480V |  | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 C COPPER WIRE ONLY | RLW-02P10_ | 22 - 10 | 4.5 | LRD05 | 18 - 8 | 15 | LC1D09 | 18 - 10 | 15 | 14 - 10 | 35 | 16 - 10 | 35
D002 | B002 |  | RLW-03P40_ |  |  | LRD06 | [5 empty] | OR | OR | OR | OR
D003 | B003 |  | RLW-04P80_ |  |  | LRD07 | [5 empty] | 8 | 40 | 8 | 40
D004 | B004 |  | RLW-07P60_ | [8 empty] | OR | OR | OR | OR
D006 | B007 |  | RLW-00110_ |  |  | LRD1508 | [5 empty] | 6 - 4 | 45 | 6 - 4 | 45
D007 | [11 empty] | OR | OR
D010 | B011 |  | RLW-00140_ |  |  | LRD1510 | [5 empty] | 2 - 1/0 | 50
| B014 |  | RLW-00210_ | 14 - 6 | 16 | LRD1512 |  |  | LC1D18 | 18 - 8
D016 | [5 empty] | LRD1514
| B021 |  | RLW-00280_ |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20
D024 |  |  | RLW-00350_
| B027 |  |  |  |  | LRD1521 |  |  | LC1D32
D030 |  |  | RLW-00460_
| B034 | [7 empty] | LC1D40 | 16 - 2 | 70 | 14 - 2/0 | 120 | 14 - 10 | 35
| B040 |  | RLW-00550_ | 6 - 4 | 45 | LRD1522 | [7 empty] | OR | OR
D046 |  |  | RLW-00650_ | OR | OR |  |  |  | LC1D50 |  |  |  |  | 8 | 40
| B052 |  |  | 2 - 1/0 | 50 | LRD1532 | [7 empty] | OR | OR
D059 |  |  | RLW-00830_ | [10 empty] | 6 - 2/0 | 120
| B065 |  |  |  |  | LRD340L | 16 - 2 | 70 | LC1D65
D074 | B077 |  | RLW-01040_ | [5 empty] | LC1D80 | 10 - 2 | 100
D088 | B096 |  | RLW-01300_ | 2, 1, | 150, | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil
D114 | B124 |  | RLW-01600_ | 1/0, 2/0, | 180, | LRD365L
D143 |  |  | RLW-02000_ | OR | OR | LR2D3563 | 10 - 1/0 | 100 |  |  |  | (1-2) x (6 - 250 kcmil) | (1-2) x 275 | 6 - 350 kcmil | 275
| B156 |  |  | 3/0, 4/0 | 250 | LR9-F5567 | 6 - 3/0 | 200
D169 | B180 |  | RLW-02500_ | 3/0, 4/0, | 250,
| B240 |  | RLW-03220_ | (250 - 350) kcmil | 325 | LR9-F5569 |  |  | LC1F500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
|  |  |  | OR | OR
|  |  |  | (400 - 500) kcmil | 375
D211 |  |  | RLW-03220_ | (1-2) x (6 - 350 kcmil) | (1-2) x 375
D273 |  |  | RLW-04140_
| B302 |  |  |  |  | LR9-F5571 | 6 - 300 kcmil | 275
D343 | B361 |  | RLW-05150_
D396 | B414 |  | RLW-06000_ | CUSTOMER TO SUPPLY
| B477 |  |  | A UL LISTED |  | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
| B515 |  | RLW-07500_ | CLOSED-LOOP
| B590 |  |  | CONNECTOR
TITLE:
CUSTOMER CONNECTION
Z1000 CONFIGURED
40C
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00429
DRAWN BY:
D.R. CMELAK
CHECKED:
K. MALUSIC
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
D.R. CMELAK
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
07/30/13
DATE:
07/30/13
DATE:
DATE:
07/30/13
DATE:
07/30/13
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
DRC
7/30/13
REVISIONS