## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE.
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE.
TABLE 1 |  | A.C. LINE WIRING
P1000 BYPASS MODEL NO. BASE NUMBER P1B_XXXX |  | WITH STANDARD, OR OPTION PM, CIRCUIT BREAKER CB1
208V | 480V | MFG. PART NUMBER |  | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) |  | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | H_ _36015 |  | 15 | 14 - 10 OR 8 - 3/0 |  | 50 OR 120
D003 | B002
D004 | B003
B004
D006 | B007 | H_ _36020 |  | 20
D007
D010 | B011 | H_ _36025 |  | 25
| B014 | H_ _36035 |  | 35
D016 |  | H_ _36040 |  | 40
| B021 | H_ _36050 |  | 50
D024 | B027 | H_ _36060 |  | 60
D030 | B034 | H_ _36070 |  | 70
| B040 | H_ _36080 |  | 80
D046 | B052 | H_ _36110 |  | 110
D059 |  | H_ _36125 |  | 125
| B065 | H_ _36150 |  | 150
B077
B096
D074
D088
D114
| B124 | J_ _36250 |  | 250 | 4 - 4/0 |  | 225
D143 | B156 |  |  |  | 3/0 - 350 kcmil |  | 225
D169 | B180
D211 |  | L_ _36400U31X |  | 400 | (1-2) x (2/0 - 500 kcmil) |  | (1-2) x 442
D273 | B240 | L_ _36600U31X |  | 600
B302
D343 | B361 | P_ _34060 |  | 600 | (1-3) x (3/0 - 500 kcmil) |  | (1-3) x 450
D396 | B414
| B477 | P_ _34080 |  | 800
B515
B590
TABLE 2 |  | A.C. MOTOR WIRING | [8 empty] | EARTH GROUND WIRING |  | CONTROL WIRING
P1000 BYPASS MODEL NO. BASE NUMBER P1B_XXXX |  | STANDARD BYPASS MOTOR OVERLOAD RELAY |  |  | OR, WITH OPTION PA MOTOR OVERLOAD RELAYS |  |  | OR, WITH OPTION PY A.C. CONTACTORS |  |  | GROUND LUG |  | DRIVE A1 AND PANEL MOUNTED TERMINAL BLOCK TB1 |  | BYPASS CONTROL PCB A2 TERMINAL BLOCKS TB1 - TB3
208V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B001 | LRD06 | 18 - 8 | 15 | LRD05 | 18 - 8 | 15 | LC1D09 | 18 - 10 | 15 | 14 - 10 | 35 | 24 - 16 | 4.4 - 5.3 | 26 - 12 | 4
D002 | B002 | LRD07 |  |  | LRD06
D003 | B003 | LRD15 |  |  | LRD07
D004 | B004 | [9 empty] | OR | OR
D006 | B007 |  |  |  | LRD1508
D007
D010 | B011 |  |  |  | LRD1510 | [5 empty] | 8 | 40
| B014 |  |  |  | LRD1512 |  |  | LC1D18 | 18 - 8
D016 |  |  |  |  | LRD1514
D024 | B021 |  |  |  | LRD1516 |  |  | LC1D25 | 14 - 6 | 20 | OR | OR
D030 | B027 |  |  |  | LRD1521 |  |  | LC1D32
| B034 | LRD340L | 16 - 2 | 70 |  |  |  | LC1D40 | 16 - 2 | 70
| B040 |  |  |  | LRD1522 | [5 empty] | 6 - 4 | 45
D046 |  | LRD350L | [5 empty] | LC1D50
D059 | B052 | LRD365L |  |  | LRD1532
| B065 | LR2 D35 | 10 - 1/0 | 100 | LRD340L | 16 - 2 | 70 | LC1D65 |  |  | OR | OR
D074 | B077 | [6 empty] | LC1D80 | 10 - 2 | 100
D088 | B096 | LR9-F5567 | 6 - 3/0 | 200 | LRD350L |  |  | LC1D115 | (1) 8 - 1/0 & (1) 8 - 250 kcmil
D114 | B124 | LR9-F5569 |  |  | LRD365L | [5 empty] | 2 | 50
D143 |  |  |  |  | LR9-F5567 | 6 - 3/0 | 200 |  |  |  | 14 - 2/0 | 120
D169 | B156 | LR9-F5571 | 6 - 300 kcmil | 275
B180
D211 | B240 | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 | LR9-F5569 |  |  | LC1F500 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
D273
D343 | B302 | LR9-F7579 |  |  | LR9-F5571 | 6 - 300 kcmil | 275
D396 | B361
| B414 | LR9-F7581 | (1-3) x (2 - 600 kcmil) | (1-3) x 500
| B477 |  |  |  | LR9-F7575 | (1-2) x (2 - 600 kcmil) | (1-2) x 500 |  |  |  | 6-250 kcmil | 275
B515
B590
TITLE:
CUSTOMER CONNECTION
P1000 BYPASS
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00447
DRAWN BY:
D.R. CMELAK
CHECKED:
D. PACKER
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
D.R. CMELAK
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
11/12/13
DATE:
11/12/13
DATE:
DATE:
11/12/13
DATE:
11/12/13
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
DRC
11/12/13
REVISIONS