## UDE00484_03
Z1000U CONFIGURED |  |  | POWER |  |  |  | SIGNAL |  |  | CONTROL |  |  | EXTERNAL POWER | GROUND
|  |  | 105°C PVC, FOR 18 AWG TO 350 MCM (BLACK) SEE NOTE 6 |  |  |  | UWR-0639 | UWR-1554 | UWR-1555 | UWR-0641 | M3508 1180001 | M3508 1180009 | M3508 1180006 | M3508_ _ _ _ _ _ _
INPUT VOLTS | DRIVE PART NO. CIMR-ZU_ _ (SEE NOTE 5) | Z1000U STD. BASE. NO. | INPUT WIRING | OUTPUT WIRING |  | TO CPT (F_)/(H_) | JUMPER DSR+, DSR-WIRE NO. A_, F_, H_, R_, S_, _V, 1-99 (BLUE) | 2 COND. 22 AWG SHIELDED (SEE NOTE 3) WIRE NO. DSR+, DSR- | TO SPEED POT R1 3 COND. 22 AWG SHIELDED (SEE NOTE 4) WIRE NO. A1, AC, +V | WIRE NO. D_ (BLUE) | TO CPT(X2) WIRE NO. 100-109 (WHITE) | WIRE NO. M_, 110-599 (RED) | WIRE NO. 600-799 (YELLOW) | 1140004 | 1_ _0004 (GREEN)
|  |  | STANDARD | OUTPUT AMPS | STANDARD | WIRE NO. _L_ | [7 empty] | CPT(X2), TO PANEL, CABINET, DOOR,FAN (GRN) | DRIVE GROUND GROUND TO PANEL (GRN)
|  |  | WIRE NO. _L_, |  | WIRE NO. _T_
208 | 2T0028 | D024 | 10 | 24.2 | 10 | 14 | 22 | 22 | 22 | 18 | SEE NOTE 7 | SEE NOTE 8 | 18 | 14 | 10
208 | 2T0042 | D030 | 8 | 30.8 | 8 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 8
208 | 2T0054 | D046 | 6 | 46.2 | 6 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
208 | 2T0068 | D059 | 4 | 59.4 | 4 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
208 | 2T0081 | D074 | 4 | 74.8 | 4 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
208 | 2T0104 | D088 | 4 | 88 | 2 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
208 | 2T0130 | D114 | 2 | 114 | 2 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
208 | 2T0154 | D143 | 1/0 | 143 | 1/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
208 | 2T0192 | D169 | 2/0 | 169 | 2/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 2
208 | 2T0248 | D211 | 3/0 | 211 | (2) 1/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 2
480 | 4T0011 | B011 | 14 | 11 | 14 | 14 | 22 | 22 | 22 | 18 | SEE NOTE 7 | SEE NOTE 8 | 18 | 14 | 10
480 | 4T0014 | B014 | 14 | 14 | 14 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 10
480 | 4T0021 | B021 | 12 | 21 | 10 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 10
480 | 4T0027 | B027 | 10 | 27 | 10 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 10
480 | 4T0034 | B034 | 8 | 34 | 8 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 8
480 | 4T0040 | B040 | 8 | 40 | 6 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 8
480 | 4T0052 | B052 | 8 | 52 | 6 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
480 | 4T0065 | B065 | 6 | 65 | 6 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
480 | 4T0077 | B077 | 4 | 77 | 4 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 6
480 | 4T0096 | B096 | 2 | 96 | 2 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
480 | 4T0124 | B124 | 2 | 124 | 1 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
480 | 4T0156 | B156 | 1/0 | 156 | 2/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 4
480 | 4T0180 | B180 | 3/0 | 180 | 3/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 2
480 | 4T0240 | B240 | 4/0 | 240 | (2) 1/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 1
480 | 4T0302 | B302 | (2) 2/0 | 302 | (2) 2/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 1
480 | 4T0361 | B361 | (2) 2/0 | 361 | (2) 3/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 1/0
480 | 4T0414 | B414 | (2) 4/0 | 414 | (2) 4/0 | 14 | 22 | 22 | 22 | 18 |  |  | 18 | 14 | 1/0
NOTES:
1. THE WIRE GAUGE IN THIS TABLE HAS BEEN SELECTED PER UL 508A TABLE 15.1, TABLE 28.1 AND TABLE 38.1.
2. FOR GROUND WIRE LARGER THAN 1/0, USE BLACK POWER WIRE AND ADD GREEN ELECTRICAL TAPE AT EACH END.
3. USE CLEAR CONDUCTOR FOR WIRE DSR+ AND USE BLACK CONDUCTOR FOR WIRE DSR-
4. STUB AND ADD SHRINK TUBING OVER THE SHIELD ON THE SPEED POT R1 SIDE OF THE SHIELDED CABLE.
5. T = CAN BE FILLED IN WITH EITHER AN 'E' OR 'U'.
6. USE WIRE AS FOLLOWS:
|  |  |  | GAUGE |  | WIRE NUMBER |  |  | GAUGE |  | WIRE NUMBER
|  |  |  | 18 |  | UWR-0238 |  |  | 2 |  | UWR-0246
|  |  |  | 16 |  | UWR-0239 |  |  | 1 |  | UWR-0247
|  |  |  | 14 |  | UWR-0240 |  |  | 1/0 |  | UWR-0248
|  |  |  | 12 |  | UWR-0241 |  |  | 2/0 |  | UWR-0249
|  |  |  | 10 |  | UWR-0242 |  |  | 3/0 |  | UWR-0250
|  |  |  | 8 |  | UWR-0243 |  |  | 4/0 |  | UWR-0251
|  |  |  | 6 |  | UWR-0244 |  |  | 250 kcmil |  | UWR-0660
|  |  |  | 4 |  | UWR-0245 |  |  | 350 kcmil |  | UWR-0587
7. USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING NO FUSE.
USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
8. USE 18 GAUGE RED FOR WIRING CONTAINING NO FUSE.
USE 18 GAUGE RED FOR WIRING CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
TITLE:
Z1000U
CONFIGURED
PANEL WIRING TABLE
SIZE:
C
PAGE:
1 of 1
REVISION:
05
DRAWING #:
UDE00484
DRAWN BY:
N. LAWS
CHECKED:
D.R. CMELAK
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
N. LAWS
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
2/16/15
DATE:
2/17/15
DATE:
DATE:
2/18/15
DATE:
2/16/15
ECO #
DRAWN BY
DATE
DESCRIPTION
CHANGED 3 AWG WITH 2 AWG WIRE
CHANGED 0180 INPUT GAUGE TO 3/0
M35172220002 & M35073220002 REPLACED BY UWR-1554 & UWR-1555
REV.
05
04
03
12941
12205
11429
KL
KL
PP
3/8/23
4/11/22
6/21/21
REVISIONS