## UDE00573_R00
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60 °C - 75 °C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75 °C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  | A.C. LINE WIRING
HV600 NARROW CONFIGURED MODEL NO. BASE NUMBER H6CPXXXX |  | WITH OPTION PM CIRCUIT BREAKER CB1 |  |  |  | STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1
208V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | HLL36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | OT30F3 | 30 | 14 - 4 | 55
D003 | B002
D004 | B003
D006 | B004
D007 | B007
B011
D010 |  | HLL36020 | 20
D016 | B014 | HLL36025 | 25
D024 | B021 | HLL36030 | 30
| B027 | HLL36040 | 40 |  |  | OT60F3 | 60
D030 | B034 | HLL36050 | 50
D046 | B040
| B052 | HLL36080 | 80 |  |  | OT100F3 | 100 | 8 - 1/0 | 55
D059 | B065 | HLL36110 | 110
D074 | B077
D088 |  | HLL36150 | 150
| B096 |  |  |  |  | OT200U12 | 200 | 4 - 300 | 275
D114
TABLE 2 |  | A.C. MOTOR WIRING |  |  |  | EARTH GROUND WIRING |  | CONTROL WIRING
HV600 NARROW CONFIGURED MODEL NO. BASE NUMBER H6CPXXXX |  | A1 DRIVE TERMINALS (T1,T2,T3) |  | A1 DRIVE TERMINALS (GND) |  | GROUND LUG |  | A1 TERMINAL BLOCKS TB1,TB3-TB7 |  | A1 TERMINAL BLOCK TB2 (FE)
208V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | B001 | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL. USE 75 °C COPPER WIRE ONLY |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 °C COPPER WIRE ONLY |  | 14 - 10 | 35 | 24 - 16 | 4.4 - 5.3 | 24 - 16 | 8.85 - 10.62
D003 | B002
D004 | B003 |  |  |  |  | OR | OR
D006 | B004
D007 | B007 |  |  |  |  | 8 | 40
D010 | B011
D016 | B014 |  |  |  |  | OR | OR
D024 | B021
D030 | B027 |  |  |  |  | 6 - 4 | 45
D046 | B034
D059 | B040
| B052 |  |  |  |  | OR | OR
B065
D074 | B077 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 °C COPPER WIRE ONLY
D088 | [5 empty] | 2 | 50
B096
D114
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[12 empty] | Rev | Description | ECO# | Drawn By | Date
[12 empty] | 00 | INITIAL RELEASE | - | EAA | 2020-02-03
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
EAA
02/03/20
REVISIONS
TITLE:
CUSTOMER CONNECTION
HV600 CONFIGURED
NARROW
TYPE 1
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00573
DRAWN BY:
E. ACKERMAN
CHECKED:
R. JENSEN
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
E. ACKERMAN
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
5/13/18
DATE:
2/3/20
DATE:
DATE:
2/3/20
DATE:
5/13/18