## UDE00609
| OPTION COMBINATIONS | [6 empty] | OPTION COMBINATIONS |  |  | OPTION BOARD PART NUMBERS PER OPTION CODE
CONNECT | PC, PE, |  | WITHOUT | PF |  | TB |  |  |  |  | OPTION CODE | PART NUMBER
WIRING | PJ, OR |  | OPT. PC, PD, | SEE |  | SEE |  |  |  | GAUGE/ | TA | AI-A3
GROUP NO. | PM | PD | PE, PJ, OR PM | NOTE 11 | PR | NOTE 12 |  | PJ | PL | COLOR | TC | SI-EP3
C1, C14 | X | [8 empty] | SEE | TD | SI-EN3D
C2, C14 |  | X | [5 empty] | X |  | NOTES | TE | DO-A3
C5, C14 |  |  | X | [6 empty] | 5 - 7 | TF | DI-A3
C3, C6, C15 | X |  |  | X | [5 empty] | SEE | TG | SI-N3
C4, C7, C16 | X |  |  |  | X |  |  |  | X | NOTES | TH | SI-P3
C3, C8, C15 |  | X |  | X | [5 empty] | 8 - 10 | TJ | SI-B3
C4, C9, C16 |  | X |  |  | X | [5 empty] | TL | SI-W3
C4, C6, C10, C16 | X |  |  | X | X | [5 empty] | TN | AO-A3
C4, C8, C10, C16 |  | X |  | X | X | [5 empty] | TQ | SI-EM3D
C3, C11, C15 |  |  | X | X | [6 empty] | TU | SI-J3
C4, C12, C16 |  |  | X |  | X | [5 empty] | TV | DI-101
C4, C10, C11, C16 |  |  | X | X | X | [5 empty] | TX | PG-X3
C17, C18 | [5 empty] | X
OPTION BOARD COMBINATIONS,
|  |  |  | GAUGE/ |  | GROUP |  |  |  | GAUGE/ | LOCATIONS AND REFERENCE DESIGNATORS
GROUP NO. | WIRE NO. | FROM | TO | COLOR |  | NO. | WIRE NO. | FROM | TO | COLOR | CONNECT TO DRIVE
| 1L1 | CB1(4) | A1(L1) |  |  | C14 | 1L1 | A1(L1) | T1(H1(F1)) |  | CONTROL BOARD CONNECTOR
C1 | 1L2 | CB1(5) | A1(L2) |  |  |  | 1L2 | A1(L2) | T1(HF(F2)) | SEE | CN5-A | CN5-B | CN5-C
| 1L3 | CB1(6) | A1(L3) |  |  | C15 | 2L1 | A1(L1) | T1(H1(F1)) | NOTE | AS A6 | AS A7 | AS A10
| 1L1 | S1(T1) | A1(L1) |  |  |  | 2L2 | A1(L2) | T1(HF(F2)) | 2 | TE
C2 | 1L2 | S1(T2) | A1(L2) |  |  | C16 | 3L1 | A1(L1) | T1(H1(F1)) |  |  | TN
| 1L3 | S1(T3) | A1(L3) |  |  |  | 3L2 | A1(L2) | T1(HF(F2)) |  |  |  | TX
| 2L1 | F3(2) | A1(L1) |  |  | C17 | 1L1 | SEE NOTE 12 | F8(1) | SEE NOTE 2 | TE | TN
C3 | 2L2 | F4(2) | A1(L2) |  |  |  | 1L2 |  | F9(1) |  | TE |  | TX
| 2L3 | F5(2) | A1(L3) |  |  |  | 1L3 |  | F10(1) |  |  | TN | TX
| 3L1 | L1(A2 OR U2) | A1(L1) |  |  | C18 | 4L1 | F8(1) | K1(L1) |  | TE | TN | TX
C4 | 3L2 | L1(B2 OR V2) | A1(L2) |  |  |  | 4L2 | F9(1) | K1(L2) |  | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU
| 3L3 | L1(C2 OR W2) | A1(L3) |  |  |  | 4L3 | F10(1) | K1(L3) |  | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU | TE
| 1L1 | TB2(1) | A1(L1) | [7 empty] | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU | TN
C5 | 1L2 | TB2(2) | A1(L2) | [7 empty] | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU |  | TX
| 1L3 | TB2(3) | A1(L3) | [7 empty] | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU | TN | TE
| 1L1 | CB1(4) | F3(1) | SEE | [6 empty] | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU | TE | TX
C6 | 1L2 | CB1(5) | F4(1) | NOTE | [6 empty] | TA, TC, TD, TF, TG, TH, TJ, TL, TQ OR TU | TN | TX
| 1L3 | CB1(6) | F5(1) | 1 | [6 empty] | WIRING NOTE:
| 1L1 | CB1(4) | L1(A1 OR U1) | [7 empty] | CONNECT THESE OPTION BOARDS' GREEN GROUND
C7 | 1L2 | CB1(5) | L1(B1 OR V1) | [7 empty] | WIRE TO THE GROUND TERMINAL "FE" ON THE
| 1L3 | CB1(6) | L1(C1 OR W1) | [7 empty] | DRIVE CONTROL BOARD.
| 1L1 | S1(T1) | F3(1)
C8 | 1L2 | S1(T2) | F4(1)
| 1L3 | S1(T3) | F5(1) | [7 empty] | SEND THE FOLLOWING DOCUMENTS ALONG
| 1L1 | S1(T1) | L1(A1 OR U1) | [7 empty] | WITH THE SCHEMATICS TO THE CUSTOMER
C9 | 1L2 | S1(T2) | L1(B1 OR V1) | [7 empty] | TA | TOBPC73060038
| 1L3 | S1(T3) | L1(C1 OR W1) | [7 empty] | TC | TOBPC73060089
| 2L1 | F3(2) | L1(A1 OR U1) | [7 empty] | TD | TOEPYAICOM16
C10 | 2L2 | F4(2) | L1(B1 OR V1) | [7 empty] | TE | TOBPC73060041
| 2L3 | F5(2) | L1(C1 OR W1) | [7 empty] | TF | TOBPC73060039
| 1L1 | TB2(1) | F3(1) | [7 empty] | TG | TOBPC73060084
C11 | 1L2 | TB2(2) | F4(1) | [7 empty] | TH | TOBPC73060082
| 1L3 | TB2(3) | F5(1) | [7 empty] | TJ | TOEPYEACOM08
| 1L1 | TB2(1) | L1(A1 OR U1) | [7 empty] | TL | TOBPC73060093
C12 | 1L2 | TB2(2) | L1(B1 OR V1) | [7 empty] | TN | TOBPC73060040
| 1L3 | TB2(3) | L1(C1 OR W1) | [7 empty] | TQ | TOEPYAICOM18
[11 empty] | TU | TOEPYAICOM13
[11 empty] | TV | TOEPYEAOPT07
[11 empty] | TX | TOBPC73060076
NOTES:
1. FOR WIRE GAUGE, COLOR AND TYPE, SEE THE WIRE TABLE SPECIFIED ON THE PRODUCTION ORDER
"INPUT POWER WIRES NUMBERED _L_", AS PER THE PARTICULAR STD. BASE NO., OR THE DRIVE PART NUMBER AND INPUT AMPS.
2. USE 14 AWG BLACK WIRE PART NO. M35081140003.
3. FOR THE 3 CONDUCTOR SHIELDED CABLE WIRES NUMBERED (+V, A1 AND AC), USE 22 AWG PART NUMBER M35073220002.
ADD 1/16 INCH GREEN HEAT SHRINK TUBING PART NUMBER UWS-0562 TO COVER THE SHIELD WIRE.
4. FOR THE 2 CONDUCTOR SHIELDED CABLE WIRES NUMBERED (A2 AND AC), USE 22 AWG PART NUMBER M35172220002.
ADD 1/16 INCH GREEN HEAT SHRINK TUBING PART NUMBER UWS-0562 TO COVER THE SHIELD WIRE.
WITH OPTION PJ
5. FOR WIRES NUMBERED 1 THRU 4, USE 18 AWG BLUE TWISTED PAIR WIRE PART NUMBER UWR-0196:
A. FOR WIRES NUMBERED 1 AND 3, CONNECT THE BLUE WIRE TO (A2, A3 OR A4) TERMINALS ((1) OR (IN1)), AND ((5) OR (OUT1)).
B. FOR WIRES NUMBERED 2 AND 4, CONNECT THE BLUE WIRE WITH THE WHITE STRIPE TO (A2, A3 OR A4) TERMINALS ((2) OR (IN2)), AND ((6) OR (OUT2)).
6. FOR JUMPERS J1 AND J2, USE 18 AWG RED WIRE PART NUMBER M35081180009.
7. CONNECT JUMPERS J1 AND J2 TO THE SHOP WIRING SIDE OF TB1.
WITH OPTION PL
8. FOR WIRES NUMBERED 1 THRU 4, USE 18 AWG BLUE TWISTED PAIR WIRE PART NUMBER UWR-0196:
A. FOR WIRES NUMBERED 1 AND 3, CONNECT THE BLUE WIRE TO (A2, A3 OR A4) TERMINALS ((1) OR (IN1)), AND ((5) OR (OUT1)).
B. FOR WIRES NUMBERED 2 AND 4, CONNECT THE BLUE WIRE WITH THE WHITE STRIPE TO (A2, A3 OR A4) TERMINALS ((2) OR (IN2)), AND ((6) OR (OUT2)).
9. FOR JUMPERS J1 AND J2, USE 18 AWG YELLOW WIRE PART NUMBER M35081180006.
10. CONNECT JUMPERS J1 AND J2 TO THE SHOP WIRING SIDE OF TB1.
WITH OPTIONS PE, PC, PM OR PJ
11. DRIVE INPUT FUSES F3, F4, F5 ARE INCLUDED FOR THE FOLLOWING BASE NUMBERS :
| G8C1B007 - G8C1B720 |  |  | G8C4B004 - G8C4B590
| G8C2B065 - G8C2B720 |  |  | G8C5B052 - G8C5B590
| G8C3B180 - G8C3B720 |  |  | G8C6B156 - G8C6B590
WITH OPTION TB
12. CONNECT TO THE 1L1, 1L2, 1L3 WIRE CONNECTION LOCATION THAT IS THE EASIEST TO CONNECT TO, AS PER THE SPECIFIED SCHEMATIC DIAGRAM
| G8C1A004 - G8C1A009 |  |  | G8C1B002 - G8C1B007
| G8C2A004 - G8C2A009 |  |  | G8C2B002 - G8C2B007
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE TABLE ABOVE
[14 empty] | Rev | Description | ECO# | Drawn By | Date
[14 empty] | 02 | ADDED OPTION TB WIRING | 10925 | KAP | 2020-10-28
[14 empty] | 01 | UPDATED OPTION TL DOCUMENTATION | 10581 | KG | 2020-05-12
[14 empty] | 00 | INITIAL RELEASE | - | NSL | 2018-10-19
ECO #
DRAWN BY
DATE
DESCRIPTION
ADDED OPTION TB WIRING
UPDATED OPTION TL DOCUMENTATION
INITIAL RELEASE
REV.
02
01
00
10925
10581
-
KAP
KG
NSL
10/28/20
05/12/20
10/19/18
REVISIONS
TITLE:
GA800 PANEL WIRING TABLE
SIZE:
C
PAGE:
1 of 1
REVISION:
02
DRAWING #:
UDE00609
DRAWN BY:
N. LAWS
CHECKED:
K. MALUSIC
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
N. LAWS
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
10/19/18
DATE:
10/22/18
DATE:
DATE:
10/23/18
DATE:
10/19/18