## Page 1
HV600 BYPASS |  |  | POWER |  |  |  | SIGNAL |  |  | CONTROL |  | EXTERNAL POWER | GROUND |  |  | NEUTRAL
|  |  | 105°C PVC, FOR 18 AWG TO 350 MCM (BLACK) SEE NOTE 5 |  |  |  | UWR-0639 | UWR-1554 | UWR-1555 | M3508 1__0001 | M3508 1__0009 | M3508 1180006 | M3508_ _ _ _ _ _ _ |  |  | M3508 1__0004
INPUT VOLTS | DRIVE PART NO. HV60U_ _ _ _ | HV600 STD. BASE. NO. | INPUT WIRING | OUTPUT WIRING |  | TO CPT (F_)/(H_) | JUMPER WIRE NO. A_, F_, H_, R_, S_, _V, 1-99 (BLUE) | 2 COND. 22 AWG SHIELDED (SEE NOTE 3) WIRE NO. D+, D- | TO SPEED POT R1 3 COND. 22 AWG SHIELDED (SEE NOTE 4) WIRE NO. +V, A1, AC | TO CPT(X2) WIRE NO. 100-109 (WHITE) | WIRE NO. M_, 110-599 (RED) | WIRE NO. 600-799 (YELLOW) | 1140004 | 1180004 | 1_ _0004 (GREEN) | TBN1(1) TO PANEL (GREEN)
|  |  |  | OUTPUT AMPS | WIRE NO. _T_ | WIRE NO. _L_ | [6 empty] | CPT(X2), A2 TO PANEL, CABINET, DOOR,FAN (GRN) | SPACE HEATER (GRN) | DRIVE GROUND GROUND TO PANEL (GRN)
WIRE NO. _L_
208 | 2011 | D002 | 14 | 2.4 | 14 | 14 | 22 | 22 | 22 | SEE NOTE 6 | SEE NOTE 7 | 18 | 14 | 18 | 14 | 8
208 | 2011 | D003 | 14 | 3.5 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
208 | 2011 | D004 | 14 | 4.6 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
208 | 2011 | D007 | 14 | 7.5 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
208 | 2011 | D010 | 14 | 10.6 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
208 | 2017 | D016 | 12 | 16.7 | 12 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
208 | 2024 | D024 | 10 | 24.2 | 10 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
208 | 2031 | D030 | 8 | 30.8 | 8 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
208 | 2046 | D046 | 8 | 46.2 | 8 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 8
208 | 2059 | D059 | 6 | 59.4 | 6 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
208 | 2075 | D074 | 4 | 74.8 | 4 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
208 | 2088 | D088 | 2 | 88 | 2 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
208 | 2114 | D114 | 1 | 114 | 2 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
208 | 2143 | D143 | 2/0 | 143 | 1/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
208 | 2169 | D169 | 3/0 | 169 | 2/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
208 | 2211 | D211 | (2) 1/0 | 211 | (2) 1/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 2 | 1/0
208 | 2273 | D273 | (2) 1/0 | 273 | (2) 1/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 2 | 1/0
240 | 2011 | A002 | 14 | 2.2 | 14 | 14 | 22 | 22 | 22 | SEE NOTE 6 | SEE NOTE 7 | 18 | 14 | 18 | 14 | 8
240 | 2011 | A003 | 14 | 3.2 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
240 | 2011 | A004 | 14 | 4.2 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
240 | 2011 | A006 | 14 | 6.8 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
240 | 2011 | A009 | 14 | 9.6 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
240 | 2017 | A015 | 12 | 15.2 | 12 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
240 | 2024 | A022 | 10 | 22 | 10 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
240 | 2031 | A028 | 8 | 28 | 10 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
240 | 2046 | A042 | 8 | 42 | 8 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 8
240 | 2059 | A054 | 6 | 54 | 6 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
240 | 2075 | A068 | 4 | 68 | 4 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
240 | 2088 | A080 | 4 | 80 | 4 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
240 | 2114 | A104 | 2 | 104 | 2 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
240 | 2143 | A130 | 1/0 | 130 | 1 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
240 | 2169 | A154 | 2/0 | 154 | 2/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
240 | 2211 | A192 | 3/0 | 192 | 3/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 2 | 1/0
240 | 2273 | A248 | (2) 1/0 | 248 | (2) 1/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 2 | 1/0
NOTES:
1. THE WIRE GAUGE IN THIS TABLE HAS BEEN SELECTED PER UL 508A TABLE 15.1, TABLE 28.1 AND TABLE 38.1.
2. FOR GROUND WIRE LARGER THAN 1/0, USE BLACK POWER WIRE AND ADD GREEN ELECTRICAL TAPE AT EACH END.
3. USE CLEAR CONDUCTOR FOR WIRE D- AND USE BLACK CONDUCTOR FOR WIRE D+
4. STUB AND ADD SHRINK TUBING OVER THE SHIELD ON THE SPEED POT R1 SIDE OF THE SHIELDED CABLE.
5. USE WIRE AS FOLLOWS:
|  |  |  | GAUGE |  | WIRE NUMBER |  | GAUGE |  | WIRE NUMBER
|  |  |  | 18 |  | UWR-0238 |  | 3 |  | UWR-0396
|  |  |  | 16 |  | UWR-0239 |  | 2 |  | UWR-0246
|  |  |  | 14 |  | UWR-0240 |  | 1 |  | UWR-0247
|  |  |  | 12 |  | UWR-0241 |  | 1/0 |  | UWR-0248
|  |  |  | 10 |  | UWR-0242 |  | 2/0 |  | UWR-0249
|  |  |  | 8 |  | UWR-0243 |  | 3/0 |  | UWR-0250
|  |  |  | 6 |  | UWR-0244 |  | 4/0 |  | UWR-0251
|  |  |  | 4 |  | UWR-0245 |  | 250 kcmil |  | UWR-0660
[8 empty] | 350 kcmil |  | UWR-0587
6. USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING NO FUSE.
USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
7. USE 18 GAUGE RED FOR WIRING CONTAINING NO FUSE.
USE 18 GAUGE RED FOR WIRING CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE TABLE ABOVE - See Dave P with Questions
[17 empty] | Rev | DESCRIPTION | ECO# | DRAWN BY | DATE
[17 empty] | 06 | UPDATED TBN1 WIRE VALEU FOR B240 | 15525 | MD | 2026-09-02
[17 empty] | 05 | REMOVED UWR-0641 AND ADJUSTED VALUES | 12805 | KJL | 2023-01-18
[17 empty] | 04 | CHANGE/REMOVE 3 AWG WIRE | 12646 | MDK | 2022-10-18
TITLE:
HV600
TYPE 3R BYPASS
PANEL WIRING TABLE
SIZE:
C
PAGE:
1 of 2
REVISION:
06
DRAWING #:
UDE00642
DRAWN BY:
N. LAWS
CHECKED:
K. PEOPLES
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
N. LAWS
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
8/13/20
DATE:
8/17/20
DATE:
DATE:
8/18/20
DATE:
8/13/20
ECO#
DRAWN BY
DATE
DESCRIPTION
UPDATED TBN1 WIRE VALEU FOR B240
REMOVED UWR-0641 AND ADJUSTED VALUES
CHANGE/REMOVE 3 AWG WIRE
Rev
06
05
04
15525
12805
12646
MD
KJL
MDK
09/02/26
01/18/23
10/18/22
REVISIONS

## Page 2
HV600 BYPASS |  |  | POWER |  |  |  | SIGNAL |  |  | CONTROL |  | EXTERNAL POWER | GROUND |  |  | NEUTRAL
|  |  | 105°C PVC, FOR 18 AWG TO 350 MCM (BLACK) SEE NOTE 5 |  |  |  | UWR-0639 | UWR-1554 | UWR-1555 | M3508 1__0001 | M3508 1__0009 | M3508 1180006 | M3508_ _ _ _ _ _ _ |  |  | M3508 1__0004
INPUT VOLTS | DRIVE PART NO. HV60U_ _ _ _ | HV600 STD. BASE. NO. | INPUT WIRING | OUTPUT WIRING |  | TO CPT (F_)/(H_) | JUMPER WIRE NO. A_, F_, H_, R_, S_, _V, 1-99 (BLUE) | 2 COND. 22 AWG SHIELDED (SEE NOTE 3) WIRE NO. D+, D- | TO SPEED POT R1 3 COND. 22 AWG SHIELDED (SEE NOTE 4) WIRE NO. +V, A1, AC | TO CPT(X2) WIRE NO. 100-109 (WHITE) | WIRE NO. M_, 110-599 (RED) | WIRE NO. 600-799 (YELLOW) | 1140004 | 1180004 | 1_ _0004 (GREEN) | TBN1(1) TO PANEL (GREEN)
|  |  |  | OUTPUT AMPS | WIRE NO. _T_ | WIRE NO. _L_ | [6 empty] | CPT(X2), A2 TO PANEL, CABINET, DOOR,FAN (GRN) | SPACE HEATER (GRN) | DRIVE GROUND GROUND TO PANEL (GRN)
WIRE NO. _L_
480 | 4005 | B1P1 | 14 | 1.1 | 14 | 14 | 22 | 22 | 22 | SEE NOTE 6 | SEE NOTE 7 | 18 | 14 | 18 | 14 | 8
480 | 4005 | B001 | 14 | 1.6 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
480 | 4005 | B002 | 14 | 2.1 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
480 | 4005 | B003 | 14 | 3.4 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
480 | 4005 | B004 | 14 | 4.8 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 14 | 8
480 | 4008 | B007 | 14 | 7.6 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
480 | 4011 | B011 | 14 | 11 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
480 | 4014 | B014 | 14 | 14 | 14 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 10 | 8
480 | 4021 | B021 | 10 | 21 | 10 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
480 | 4027 | B027 | 10 | 27 | 10 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
480 | 4034 | B034 | 8 | 34 | 8 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 8 | 8
480 | 4040 | B040 | 8 | 40 | 8 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 8
480 | 4052 | B052 | 6 | 52 | 6 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
480 | 4065 | B065 | 4 | 65 | 6 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
480 | 4077 | B077 | 4 | 77 | 4 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
480 | 4096 | B096 | 2 | 96 | 2 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 6 | 6
480 | 4124 | B124 | 1 | 124 | 1 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
480 | 4156 | B156 | 2/0 | 156 | 2/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
480 | 4180 | B180 | 3/0 | 180 | 3/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 4 | 1/0
480 | 4240 | B240 | (2) 1/0 | 240 | (2) 1/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 2 | 1/0
480 | 4302 | B302 | (2) 2/0 | 302 | (2) 2/0 | 14 | 22 | 22 | 22 |  |  | 18 | 14 | 18 | 1 | 2/0
NOTES:
1. THE WIRE GAUGE IN THIS TABLE HAS BEEN SELECTED PER UL 508A TABLE 15.1, TABLE 28.1 AND TABLE 38.1.
2. FOR GROUND WIRE LARGER THAN 1/0, USE BLACK POWER WIRE AND ADD GREEN ELECTRICAL TAPE AT EACH END.
3. USE CLEAR CONDUCTOR FOR WIRE D- AND USE BLACK CONDUCTOR FOR WIRE D+
4. STUB AND ADD SHRINK TUBING OVER THE SHIELD ON THE SPEED POT R1 SIDE OF THE SHIELDED CABLE.
5. USE WIRE AS FOLLOWS:
|  |  |  | GAUGE |  | WIRE NUMBER |  | GAUGE |  | WIRE NUMBER
|  |  |  | 18 |  | UWR-0238 |  | 3 |  | UWR-0396
|  |  |  | 16 |  | UWR-0239 |  | 2 |  | UWR-0246
|  |  |  | 14 |  | UWR-0240 |  | 1 |  | UWR-0247
|  |  |  | 12 |  | UWR-0241 |  | 1/0 |  | UWR-0248
|  |  |  | 10 |  | UWR-0242 |  | 2/0 |  | UWR-0249
|  |  |  | 8 |  | UWR-0243 |  | 3/0 |  | UWR-0250
|  |  |  | 6 |  | UWR-0244 |  | 4/0 |  | UWR-0251
|  |  |  | 4 |  | UWR-0245 |  | 250 kcmil |  | UWR-0660
[8 empty] | 350 kcmil |  | UWR-0587
6. USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING NO FUSE.
USE 18 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE WHITE FOR WIRING TO CPT(X2) OF A CIRCUIT CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
7. USE 18 GAUGE RED FOR WIRING CONTAINING NO FUSE.
USE 18 GAUGE RED FOR WIRING CONTAINING A FUSE RATED 7 AMPS, OR LESS.
USE 16 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 7 AMPS, AND LESS THAN OR EQUAL TO 10 AMPS.
USE 14 GAUGE RED FOR WIRING CONTAINING A FUSE RATED GREATER THAN 10 AMPS, AND LESS THAN OR EQUAL TO 15 AMPS.
[17 empty] | 06 | REMOVED UWR-0641 AND ADJUSTED VALUES | 12805 | KJL | 2023-01-18
TITLE:
HV600
TYPE 3R BYPASS
PANEL WIRING TABLE
SIZE:
C
PAGE:
2 of 2
REVISION:
06
DRAWING #:
UDE00642
DRAWN BY:
N. LAWS
CHECKED:
K. PEOPLES
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
N. LAWS
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
8/13/20
DATE:
8/17/20
DATE:
DATE:
8/18/20
DATE:
8/13/20