## Page 1
`
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  |  | A.C. LINE WIRING
FP605 BYPASS MODEL NO. BASE NUMBER F6B3XXXX |  |  | WITH OPTION PC, PE, OR PM, TO CIRCUIT BREAKER CB1 |  |  |  | OR, STANDARD, TO DISCONNECT SWITCH S1
208V | 240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | H_ _36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120
D003 | A003 | B001
D004 | A004 | B002
B003
B004
B007
D007 | A006 |  | H_ _36020 | 20
D010 | A009 | B011 | H_ _36025 | 25
|  | B014 | H_ _36030 | 30
D016 | A015 |  | H_ _36035 | 35
|  | B021 | H_ _36040 | 40
| A022 |  | H_ _36045 | 45
D024 |  | B027 | H_ _36050 | 50
D030 | A028 |  | H_ _36060 | 60
|  | B034 | H_ _36070 | 70
| A042 | B040 | H_ _36080 | 80
D046 |  |  | H_ _36090 | 90
| A054 | B052 | H_ _36100 | 100
D059 |  |  | H_ _36110 | 110
| A068 | B065 | H_ _36125 | 125
D074 | A080 | B077 | H_ _36150 | 150
D088 | A104 | B096 | H_ _36150M74 | 150
D114 | [6 empty] | J_ _36000S17 | 175 | 4 - 4/0 | 225
|  | B124 | JLL36250M75 | 250 | 4 - 4/0 | 225
| A130 | [5 empty] | J_ _36000S25LY | 250
D143 | A154 | B156 |  |  | 3/0 - 350 kcmil | 225 | J_ _36000S25 |  | 3/0 - 350 kcmil | 225
D169 |  | B180
D211 | A192 |  | L_ _36400U31X | 400 | (1 - 2) x (2/0-500 kcmil) | (1 - 2) x 442 | L_ _36000S40X | 400 | (1 - 2) x (2/0-500 kcmil) | (1 - 2) x 442
D273 | A248 | B240 | L_ _36600U31X | 600
|  | B302 |  |  |  |  | L_ _36000S60X | 600 | (1 - 2) x (2/0-500 kcmil) | (1 - 2) x 442
TABLE 2 |  |  | A.C. MOTOR WIRING
FP605 BYPASS MODEL NO. BASE NUMBER F6B3XXXX |  |  | MOTOR CONNECTION TERMINAL BLOCK TB3
208V | 240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | NDN111A-WH | 14 - 2 | 32
D003 | A003 | B001
D004 | A004 | B002
D007 | A006 | B003
D010 | A009 | B004
D016 | A015 | B007
D024 | A022 | B011
D030 | A028 | B014
D046 | A042 | B021
D059 | A054 | B027
| A068 | B034
B040
B052
B065
D074 | A080 | B077 | MPDB63153 | 14 - 8 OR 6 - 2/0 | 50 OR 120
D088 | A104 | B096
D114 |  |  | 1323572 | 14 - 10 OR 8 OR 6 - 2/0 | 35 OR 40 OR 120
| A130 | B124 | MPDB67523 | (2) 6 OR (2) 4 OR (2) 3 - 4/0 | (2) 80 OR (2) 100 OR (2) 150
D143 | A154 | B156
D169 | A192 | B180
D211 | A248 | B240 | 1333320 | (2) 6 - 250 | (2) 275
D273 |  | B302
TABLE 3 |  |  | EARTH GROUND WIRING |  |  |  | NEUTRAL |  | CONTROL WIRING
FP605 BYPASS MODEL NO. BASE NUMBER F6B3XXXX |  |  | INPUT GROUND LUG |  | MOTOR CONNECTION GROUND LUG |  | TERMINAL BLOCK TBN1 |  | A1 DRIVE TERMINAL BLOCKS TB1,TB3-TB6 |  | A1 DRIVE TERMINAL BLOCK TB2 (FE) |  | DIN RAIL MOUNTED TERMINAL BLOCK TB4 |  | A2 BYPASS CONTROL PCB TERMINAL BLOCKS TB1-TB4, TB6
208V | 240V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | 14 - 10 OR 8 OR 6 - 4 OR 2 - 1/0 | 35 OR 40 OR 45 OR 50 | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | 16 - 10 OR 8 OR 6 - 4 | 35 OR 40 OR 45 | 24 - 16 | 4.4 - 5.3 | 24 - 18 | 8.9 - 10.7 | 26 - 10 | 5.3 - 7.1 | 26 - 14 | 4
D003 | A003 | B001
D004 | A004 | B002
D007 | A006 | B003
D010 | A009 | B004
D016 | A015 | B007
D024 | A022 | B011
D030 | A028 | B014
B021
B027
B034
D046 | A042 | B040 |  |  |  |  | 14 - 10 OR 8 OR 6 - 2/0 | 35 OR 40 OR 120
D059 | A054 | B052
D074 | A068 | B065
D088 | A080 | B077
D114 | A104 | B096
B124
D143 | A130 |  | 14 - 2/0 | 120 |  |  | 6 - 350 kcmil | 275
D169 | A154 | B156
D211 | A192 | B180 | 6 - 250 kcmil | 275 | 6 - 250 kcmil | 275
D273 | A248 | B240
B302
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[17 empty] | Rev | Description | ECO# | Drawn By | Date
[17 empty] | 00 | INITIAL RELEASE | -- | EAA | 2022-09-20
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
--
EAA
09/20/22
REVISIONS
TITLE:
CUSTOMER CONNECTION
FP605 BYPASS
TYPE 3R RATING
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00744
DRAWN BY:
E. ACKERMAN
CHECKED:
K. MALUSIC
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
E. ACKERMAN
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
7/6/22
DATE:
9/1/22
DATE:
DATE:
9/20/22
DATE:
7/6/22

## Sheet2
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 3 |  | A.C. MOTOR WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C3XXXX |  | WITH OPTION PH, TO LOAD REACTOR L4 |  |  | OR, WITHOUT OPTION PH, TO STANDARD AC DRIVE
240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB. - IN.)
| B002 | RLW-03P40_ | 22 - 10 | 4.5 | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL USE 75°C COPPER WIRE ONLY
| B003 | RLW-04P80_
| B004 | RLW-07P60_
| B007 | RLW-00110_
A006 | B011 | RLW-00140_
A009 | B014 | RLW-00210_ | 14 - 6 | 16
A015 |  | RLW-00280_
A022
A028 | B021 | RLW-00350_
B027
| B034 | RLW-00460_
A042 | B040 | RLW-00550_ | 6 - 4 OR 2 - 1/0 | 45 OR 50
| B052 | RLW-00650_
A054 | B065 | RLW-00830_
A068 | B077 | RLW-01040_
A080
A104 | B096 | RLW-01300_ | 2 - 1 OR 1/0 - 2/0 OR 3/0 - 4/0 | 150 OR 180 OR 250
A130 | B124 | RLW-01600_
A154 | B156 | RLW-02000_
A192 |  | RLW-02500_ | 2/0 OR 3/0 - 4/0 OR 250 - 350 kcmil OR 400 - 500 kcmil | 180 OR 250 OR 325 OR 375
| B180 |  |  |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75°C COPPER WIRE ONLY
A248 | B240 | RLW-03220_
A312 | B302 | RLW-04140_ | (1-2) x (6-350 kcmil) | (1 - 2) x 375
A360 | B361 | RLW-05150_
| B414 | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR
B477
| B515 | RLW-07500_
B590
| B720 | RL-7500_
TABLE 4 |  | EARTH GROUND WIRING |  | NEUTRAL |  | CONTROL WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C3XXXX |  | GROUND LUGS |  | TERMINAL BLOCK TBN1 |  | TERMINAL BLOCK TB1
240 V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B002 | 14 - 10 OR 8 OR 6 - 4 OR 2 - 1/0 | 35 OR 40 OR 45 OR 50 | 16 - 10 OR 8 OR 6 - 4 | 35 OR 40 OR 45 | 26 - 10 | 5.3 - 7.1
A004 | B003
A006 | B004
A009 | B007
A015 | B011
A022 | B014
A028 | B021
B027
B034
B040
A042 |  | 14 - 2/0 | 120 | 14 - 10 OR 8 OR 6 - 2/0 | 35 OR 40 OR 120
A054 | B052
A068 | B065
A080 | B077
A104 | B096
A130 | B124
A154 | B156
A192 | B180 | 6 - 250 kcmil | 275 | 6 - 350 kcmil | 275
A248 | B240
A312 | B302
A360 | B361
B414
B477
B515
B590
B720
TITLE:
CUSTOMER CONNECTION
FP605 CONFIGURED
TYPE 3R ND RATING
SIZE:
C
PAGE:
2 of 2
REVISION:
00
DRAWING #:
UDE00744
DRAWN BY:
E. ACKERMAN
CHECKED:
K. MALUSIC
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
E. ACKERMAN
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
7/6/22
DATE:
6/13/18
DATE:
DATE:
6/14/18
DATE:
7/6/22