## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  |  | A.C. LINE WIRING
FP605 BYPASS MODEL NO. BASE NUMBER F6B1XXXX |  |  | WITH OPTION PC, PE OR PM CIRCUIT BREAKER CB1 |  |  |  | OR, STANDARD NON-FUSED DISCONNECT SWITCH S1
208V | 240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | V0 | 20 | 14 - 8 | 19
D003 | A003 | B001
D004 | A004 | B002
B003
B004
D007 | A006 | B007 | H_ _36020 | 20
D010 | A009 | B011 | H_ _36025 | 25
| A015 | B014 | H_ _36035 | 35
D016 |  |  | H_ _36040 | 40
| A022 | B021 | H_ _36050 | 50 |  |  | V3 | 45 | 10 OR 8 OR 6 - 2 | 35 OR 40 OR 50
D024 |  | B027 | H_ _36060 | 60
| A028 |  | H_ _36070 | 70
D030 |  | B034 |  |  |  |  | V4 | 63
|  | B040 | H_ _36080 | 80
| A042 |  | H_ _36100 | 100 |  |  | V5 | 100 | 8 - 2/0 | 200
D046 |  | B052 | H_ _36110 | 110
D059 | A054 |  | H_ _36125 | 125
| A068 | B065 | H_ _36150 | 150
D074 | A080 | [5 empty] | V6 | 115
D088 |  | B077 |  |  |  |  | H_ _36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120
B096
D114 | A104 | [5 empty] | J_ _36000S17 | 175 | 4 - 4/0 | 225
|  | B124 | J_ _36250 | 250 | 4 - 4/0 | 225
| A130 | [5 empty] | J_ _36000S25 | 250 | 3/0 - 350 kcmil
D143 | A154 | B156 |  |  | 3/0 - 350 kcmil
D169 |  | B180
| A192 |  | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D211 | [6 empty] | L_ _36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D273 | A248 | B240 | L_ _36600U31X | 600
|  | B302 |  |  |  |  | L_ _36000S60X | 600
TABLE 2 |  |  | A.C. MOTOR WIRING |  |  | EARTH GROUND WIRING |  | CONTROL WIRING
FP605 BYPASS MODEL NO. BASE NUMBER F6B1XXXX |  |  | WITH STANDARD MOTOR TERMINAL BLOCK TB3 |  |  | GROUND LUG |  | A1 TERMINAL BLOCKS TB1,TB3-TB6 |  | A1 TERMINAL BLOCK TB2 (FE) |  | A2 TERMINAL BLOCKS TB1-TB4 AND TB6 |  | PANEL TERMINAL BLOCK TB4
208V | 240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | NDN111A-WH | 14 - 2 | 32 | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | 24 - 16 | 4.4 - 5.3 | 24 - 18 | 8.9 - 10.7 | 26 - 14 | 4 | 26 - 10 | 5.3 - 7.1
D003 | A003 | B001
D004 | A004 | B002
D007 | A006 | B003
D010 | A009 | B004
D016 | A015 | B007
D024 | A022 | B011
D030 | A028 | B014
D046 | A042 | B021
D059 | A054 | B027
| A068 | B034
B040
B052
B065
D074 | A080 | B077 | MPDB63153 | 14 - 8 OR 6 - 2/0 | 50 OR 120
D088 | A104 | B096
D114 |  |  | 1323572 | 14 - 10 OR 8 OR 6 - 2/0 | 35 OR 40 OR 120
| A130 | B124 | MPDB67523 | (1-2) x (6) OR (4) OR (3 - 4/0) | (1-2) x 80 OR 100 OR 150
D143 | A154 | B156
D169
| A192 | B180 |  |  |  | 14 - 2/0 | 120
D211 | A248 | B240 | MPDB69093 | (1-2) x (4 - 500 kcmil) | (1-2) x 500
D273 |  | B302
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE
[16 empty] | Rev | Description | ECO# | Drawn By | Date
[16 empty] | 02 | UPDATE OBSOLETE MARATHON TB3 | 13766 | JZ | 2024-04-17
[16 empty] | 01 | UPDATE OBSOLETE MARATHON TB3 | 13612 | JZ | 2024-02-01
[16 empty] | 00 | INITIAL RELEASE | - | KM | 2022-11-16
ECO #
DRAWN BY
DATE
DESCRIPTION
UPDATE OBSOLETE MARATHON TB3
UPDATE OBSOLETE MARATHON TB3
INITIAL RELEASE
REV.
02
01
00
13766
13612
-
JZ
JZ
KM
4/17/24
02/01/24
11/16/22
REVISIONS
TITLE:
CUSTOMER
CONNECTION
FP605 BYPASS
TYPE 1
SIZE:
C
PAGE:
1 of 1
REVISION:
02
DRAWING #:
UDE00755
DRAWN BY:
K. MALUSIC
CHECKED:
K. PEOPLES
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
K. MALUSIC
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
11/16/22
DATE:
11/16/22
DATE:
DATE:
11/16/22
DATE:
11/16/22