## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  |  | A.C. LINE WIRING
FP605 CONFIGURED MODEL NO. BASE NUMBER F6C1XXXX |  |  | WITH OPTION PC, PE OR PM CIRCUIT BREAKER CB1 |  |  |  | OR, OPTION PD NON-FUSED DISCONNECT SWITCH S1 |  |  |  | OR, WITHOUT OPTIONS PE, PC, PM OR PD TO INPUT POWER TERMINAL BLOCK TB2
208V | 240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | OT30F3 | 30 | 14 - 4 | 55 | NDN111A-WH-P | 90 | 14 - 2 | 32
D003 | A003 | B001
D004 | A004 | B002
D007 | A006 | B003
| A009 | B004
B007
B011
D010 |  |  | H_ _36020 | 20
D016 | A015 | B014 | H_ _36025 | 25
D024 | A022 | B021 | H_ _36030 | 30
|  | B027 | H_ _36040 | 40 |  |  | OT60F3 | 60
D030 | A028 | B034 | H_ _36050 | 50
| A042 | B040
D046 |  |  | H_ _36060 | 60
|  | B052 | H_ _36080 | 80 |  |  | OT100F3 | 100 | 8 - 1/0
D059 | A054 | B065 | H_ _36110 | 110
D074 | A068
|  | B077 | [8 empty] | MPDB63153 | 175 | 14 - 8 OR 6 - 2/0 | 50 OR 120
D088 | A080 |  | H_ _36150 | 150
D114 | A104 | B096 |  |  |  |  | H_ _36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120
B124
| A130 |  | J_ _36200LY | 200 | 4 - 4/0 | 225 | OT200U12 | 200 | 4 - 300 kcmil | 275
D143 |  | B156 | [8 empty] | MPDB67003 | 310 | 6 - 350 kcmil | 275
D169 | A154 | B180 | J_ _36250 | 250 | 3/0 - 350 kcmil
| A192 | [5 empty] | J_ _36000S25 | 250 | 3/0 - 350 kcmil | 225
D211 |  |  | J_ _36250C
D273 | A248 | B240 | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442 | L_ _36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442 | MPDB69123 | 620 | (1-2) x (6 - 350 kcmil) | (1-2) x 275
| A312 | B302
D343 | A360 | B361 | L_ _36600U31X | 600 |  |  | L_ _36000S60X | 600 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
D396 |  | B414
|  | B477 | P_ _36080-PDC | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | P_ _34000S80-PDC | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | MPDB69313 | 760 | (1-2) x (4 - 500 kcmil) | (1-2) x 500
B515
|  | B590 | [8 empty] | MPDB69543 | 840 | (1-2) x (2 - 600 kcmil) | (1-2) x 600
|  | B720 | P_ _36100U44A | 1000 | (1-4) x (3/0 - 500 kcmil) | (1-4) x 450 | P_ _36000S10 | 1000 | (1-4) x (3/0 - 500 kcmil) | (1-4) x 450 | PDB-55-500-1 | 1600 | (1-5) x (3/0 - 500 kcmil) | (1-5) x 450
TABLE 2 |  |  | A.C. MOTOR WIRING
FP605 CONFIGURED MODEL NO. BASE NUMBER F6C1XXXX |  |  | WITH OPTION PH, LOAD REACTOR L4 |  |  | WITH OPTION P8 TERMINAL BLOCK TB3 |  |  | OR, WITHOUT OPTION PH, P8 TO A1 DRIVE TERMINALS (T1,T2,T3) |  | OR, WITHOUT OPTION PH, P8 TO A1 DRIVE TERMINAL (GROUND)
208V | 240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
|  | B1P1 | RLW-01P60_ | 22 - 10 | 4.5 | NDN111A-WH-P | 14 - 2 | 32 | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL. USE 75 °C COPPER WIRE ONLY |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 °C COPPER WIRE ONLY
|  | B001 | RLW-02P10_
D002 |  | B002 | RLW-03P40_
D003 | A002 | B003 | RLW-04P80_
D004 | A003 | B004 | RLW-07P60_
A004
D007 |  | B007 | RLW-00110_
D010 | A006 | B011 | RLW-00140_
D016 | A009 | B014 | RLW-00210_ | 14 - 6 | 16
| A015 |  | RLW-00280_
A022
D024 | A028 | B021 | RLW-00350_
B027
D030 |  | B034 | RLW-00460_
| A042 | B040 | RLW-00550_ | 6 - 4 OR 2 - 1/0 | 45 OR 50
D046 |  | B052 | RLW-00650_
D059 | A054 | B065 | RLW-00830_
D074 | A068 | B077 | RLW-01040_ |  |  | MPDB63153 | 14 - 8 OR 6 - 2/0 | 50 OR 120 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 °C COPPER WIRE ONLY
A080
D088 | A104 | B096 | RLW-01300_ | 2 OR 1/0 - 2/0 OR 4/0 | 150 OR 180 OR 250
|  | B124 | RL-13002 |  |  | 16303-3 | 6 - 350 | 275
D114 |  |  | RLW-01600_ |  |  | MPDB63153 | 14 - 8 OR 6 - 2/0 | 50 OR 120
| A130 |  |  | CUSTOMER TO CONNECT TO OPTION P8, TERMINAL BLOCK (TB3). USE THE CORRESPONDING TB3 WIRE RANGE AND TORQUE VALUES TO MAKE THE CUSTOMER CONNECTION. |  | MPDB67003 | 6 - 350 kcmil | 275
D143 | A154 | B156 | RLW-02000_
D169 |  | B180 | RLW-02500_
| A192 |  |  |  |  | MPDB67523 | (1-2) x (6) OR (4) OR (3 - 4/0) | (1-2) x 80 OR 100 OR 150
D211 | A248 | B240 | RLW-03220_
D273 |  |  | RLW-04140_
| A312 | B302 |  | (1-2) x (6 - 350 kcmil) | (1-2) x 375 | 16500-3 | (1-2) x (6 - 350 kcmil) | (1-2) x 275
D343 | A360 | B361 | RLW-05150_
D396
|  | B414 | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR
|  | B477 |  |  |  | 16528-3 | (1-2) x (2 - 600 kcmil) | (1-2) x 500
|  | B515 | RLW-07500_
B590
|  | B720 | RL-75002 |  |  | PDB-55-500-1 | (1-5) x (3/0 - 500 kcmil) | (1-5) x 450
TABLE 3 |  |  | EARTH GROUND WIRING |  | CONTROL WIRING
FP605 CONFIGURED MODEL NO. BASE NUMBER F6C1XXXX |  |  | GROUND LUG |  | A1 TERMINAL BLOCKS TB1,TB3-TB7 |  | A1 TERMINAL BLOCK TB2 (FE) |  | PANEL TERMINAL BLOCK TB1,TB4
208V | 240V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
D002 | A002 | B1P1 | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | 24 - 16 | 4.4 - 5.3 | 24 - 18 | 8.9 - 10.7 | 26 - 10 | 5.3 - 7.1
D003 | A003 | B001
D004 | A004 | B002
D007 | A006 | B003
D010 | A009 | B004
D016 | A015 | B007
D024 | A022 | B011
D030 | A028 | B014
D046 | A042 | B021
D059 | A054 | B027
D074 | A068 | B034
D088 | A080 | B040
D114 | A104 | B052
B065
B077
B096
B124
D143 | A130 | B156 | 14 - 2/0 | 120
D169 | A154 | B180
D211 | A192 | B240
D273 | A248 | B302
A312
D343 | A360 | B361 | 6 - 250 | 275
D396 |  | B414
B477
B515
B590
B720
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE
[15 empty] | Rev | Description | ECO# | Drawn By | Date
[15 empty] | 00 | INITIAL RELEASE | - | KM | 2022-11-16
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
KM
11/16/22
REVISIONS
TITLE:
CUSTOMER
CONNECTION
FP605 CONFIGURED
TYPE 1
SIZE:
C
PAGE:
1 of 1
REVISION:
00
DRAWING #:
UDE00757
DRAWN BY:
K. MALUSIC
CHECKED:
K. PEOPLES
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
K. MALUSIC
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
11/16/22
DATE:
11/16/22
DATE:
DATE:
11/16/22
DATE:
11/16/22