## Sheet1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 | A.C. LINE WIRING
MATRIX CONFIGURED MODEL NO. BASE NUMBER Z1EPBXXX | STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1 |  |  |  | WITH OPTION PM CIRCUIT BREAKER CB1
480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
B011 | OT30G3-3BS | 30 | 12 - 2/0. | 53 | HLL36020 | 20 | 14 - 10 OR 8 - 3/0 | 50 OR 120
B014 |  |  |  |  | HLL36025 | 25
B021 |  |  |  |  | HLL36030 | 30
B027 | OT60G3-3BS | 61 | 13 - 2/0. | 54 | HLL36040 | 40
B034 |  |  |  |  | HLL36050 | 50
TABLE 2 | EARTH GROUND WIRING |  | A.C. MOTOR WIRING | CONTROL WIRING
MATRIX CONFIGURED MODEL NO. BASE NUMBER Z1EPBXXX | GROUND LUG |  | TO STANDARD AC DRIVE | A1 TERMINAL BLOCK TB1 - TB4 |  | A1 TERMINAL BLOCK TB5
480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) |  | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
B011 | 14 -10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 C COPPER WIRE ONLY | 24 - 16 | 4.4 - 5.3 | 20 - 14 | 4.4 - 8.9
B014
B021
B027
B034
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[9 empty] | Rev | Description | ECO# | Drawn By | Date
[9 empty] | 00 | INITIAL RELEASE | - | LMM | 2026-06-03
ECO #
DRAWN BY
DATE
DESCRIPTION
INITIAL RELEASE
REV.
00
-
LMM
06/03/26
REVISIONS
TITLE:
CUSTOMER CONNECTION
Z1000U CONFIGURED NARROW
SIZE:
C
PAGE:
1 of 1
REVISION 00
02
DRAWING #:
UDE00816
DRAWN BY:
L. MCKEON
CHECKED:
K. MALUSIC
TECH:
APPROVED:
R. JENSEN
ORIGINAL DESIGN:
L. MCKEON
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
06/03/26
DATE:
06/05/26
DATE:
DATE:
06/05/26
DATE:
06/03/26