## Slide 1: HARMONICS
OVERVIEW AND MITIGATION TECHNIQUES
Speaker Name | Date xxx, yy 2021

## Slide 2: PRESENTATION AGENDA
Harmonics Overview
Harmonic Solutions
Notes: General overview of presentation.

## Slide 3
HARMONICS
OVERVIEW

## Slide 4: DRIVES & HARMONICS
HARMONICS OVERVIEW
BEFORE DRIVES…
EVERYTHING WAS SINUSOIDAL
SUPPLY LINE
Provides sinewave voltage which the motor likes
MOTOR
Draws sinewave current which the supply likes.
MOTORS RAN DIRECTLY ACROSS-THE-LINE

## Slide 5
Why
Change?

## Slide 6: BENEFITS OF DRIVES
Electric AC Motors
  Consume 45% of the world’s electrical energy.
Main Purpose of Drives
  Save Energy (Power)
Other Advantages
  Improved Efficiency
  Improved Process Control
  Reduced Maintenance on Mechanical Couplings
  Compact Design
ACROSS THE LINE
1 Fan Across the Line
100% Speed  100% Flow
= 100% Power
MOTOR RUN BY A DRIVE
70% speed  49% Torque
Total Power = 34%
66% Power Reduction
HARMONICS OVERVIEW

## Slide 7: INCREASING EFFICIENCY
Notes: In fact, we’ve calculated that our installed products have saved the equivalent of 3% of the world’s annual power consumption.
That’s the total annual power consumption of Germany!

## Slide 8: DRIVES & HARMONICS
HARMONICS OVERVIEW
NO ONE’S PERFECT…
Input Voltage
Input Current
Output Voltage
Output Current
VFDs

## Slide 9
What Causes
Harmonics?

## Slide 10: DRIVES & HARMONICS
Conventional Drive
HARMONICS OVERVIEW
DC
BUS
DIODE
BRIDGE
OUTPUT
IGBT

## Slide 11: DRIVES & HARMONICS
A diode is like a check valve
Water flows when pressure hits a certain level
What is a diode?
HARMONICS OVERVIEW

## Slide 12: DRIVES & HARMONICS
Current Draw Only Occurs When
  AC voltage > DC Voltage
AC > DC?
  +/- Peaks of AC Voltage
  Resulting Current Draw is Non-Linear
Drives draw line current when needed.
Diode Bridge
The current waveform is distorted.
Distortion  Harmonics
HARMONICS OVERVIEW

## Slide 13: DRIVES & HARMONICS
Phase A -> B Current Path: IAB
HARMONICS OVERVIEW
Diodes only allow current flow in ONE direction.
If Vab > DC BUS, then current flows
Vcap
DC BUS

## Slide 14: DRIVES & HARMONICS
Phase A -> B Current Path: IAC
HARMONICS OVERVIEW
Diodes only allow current flow in ONE direction.
If Vac > DC BUS, then current flows
Vcap
DC BUS

## Slide 15: DRIVES & HARMONICS
HARMONICS OVERVIEW
Status:
Result:
YES, WE HAVE FLOW
Supply = Load
Supply < Load
Supply > Load
NO FLOW
NO FLOW
When does current flow?
Same as diode when input voltage > DC BUs

## Slide 16
What are
HARMONICS?

## Slide 17: WHAT ARE HARMONICS?
Voltage is typically supplied as a sine wave.
Chart: 
 | 0 | 0.36812 | 0.68455 | 0.90483 | 0.99803 | 0.95106 | 0.77051 | 0.48175 | 0.12533 | -0.24869 | -0.58779 | -0.84433 | -0.98229 | -0.98229 | -0.84433 | -0.58779 | -0.24869 | 0.12533 | 0.48175 | 0.77051 | 0.95106 | 0.99803 | 0.90483 | 0.68455 | 0.36812 | -4.9615e-15 | -0.36812 | -0.68455 | -0.90483 | -0.99803 | -0.95106 | -0.77051 | -0.48175 | 0
Supply Voltage
Current Waveform ≠ Voltage Waveform
Current waveform is non-linear.
Chart: 
 | 0 | 0 | 0 | 0 | 0.99803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.98229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.99803 | 0 | 0 | 0 | 0
Non-linear Current
Harmonics occur whenever the current waveform is distorted.
Distortion  Harmonics
HARMONICS OVERVIEW

## Slide 18: WHAT ARE HARMONICS?
Fourier Series
HARMONICS OVERVIEW
Any periodic waveform can be expressed as an infinite sum of sine waves in integral multiples called “harmonics”.
Jean Baptiste Joseph Fourier (21 March 1768 – 16 May 1830)
=
+
h=1
h=5
h=7
h=11
h=13
h=17
.
.
.
Actual
Fundamental
.
.
.
Harmonics
Y(wt)
Math Used to Find a Waveform’s Components

## Slide 19
HARMONICS,
Why the Concern?

## Slide 20: WHY THE CONCERN?
Harmonic currents create heat (power loss)
Unchecked harmonics may lead to resonance with line inductance & capacitance
HARMONICS OVERVIEW
Excessive harmonics distorts input voltage
Power losses in transformers, wiring and other components on the power line
EFFECT
CAUSE
Resonance creates poor reliability, premature failure, and greater cost in maintenance and parts
Electrical equipment may operate erratically, fault, or even prematurely fail

## Slide 21: HARMONICS CAUSE HEAT?
HARMONICS OVERVIEW
All line & load currents create HEAT
Pushing current through cables, reactors, etc. will create losses in the form of heat
Only the FUNDAMENTAL does USEFUL work
Only the horizontal () effort will lift the weight
HARMONICS only
create heat
Any effort outside of horizontal movement is simply wasted energy

## Slide 22: WHY CARE?
HARMONICS OVERVIEW
Additional Cooling required due to added heating
LOWER EFFICIENCY
HIGHER OPERATING COSTS
Oversizing of transformers and other equipment
HIGHER STARTUP
REPLACEMENT COSTS
Charges or penalties from
high harmonics, low power factor
COSTLY POST INSTALL CORRECTIVE ACTIONS

## Slide 23: WHY CARE? … Transformers
Higher reactive power increases kVA.
Higher kVA requires a larger transformer.
Higher kVA can increase utility company demand charges.
Reactive power is wasted energy
HARMONICS OVERVIEW

## Slide 24: NON-LINEAR LOADING
Electronic Ballasts (Lighting)
Arc Furnaces
Switching Mode Power Supplies
  Computers, Servers, Monitors, Printers, Photocopiers, Etc.
Other Non-Linear Loads:
Drives are not the only
non-linear loads.

## Slide 25: INPUT CURRENT WHAT DO WE WANT?
Voltage is typically supplied as a sine wave.
Chart: 
 | 0 | 0.36812 | 0.68455 | 0.90483 | 0.99803 | 0.95106 | 0.77051 | 0.48175 | 0.12533 | -0.24869 | -0.58779 | -0.84433 | -0.98229 | -0.98229 | -0.84433 | -0.58779 | -0.24869 | 0.12533 | 0.48175 | 0.77051 | 0.95106 | 0.99803 | 0.90483 | 0.68455 | 0.36812 | -4.9615e-15 | -0.36812 | -0.68455 | -0.90483 | -0.99803 | -0.95106 | -0.77051 | -0.48175 | 0
Supply Voltage
Current Waveform ≠ Voltage Waveform
Current waveform is non-linear.
Chart: 
 | 0 | 0 | 0 | 0 | 0.99803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.98229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.99803 | 0 | 0 | 0 | 0
Non-linear Current
Current Waveform = Voltage Waveform
Chart: 
 | 0 | 0.36812 | 0.68455 | 0.90483 | 0.99803 | 0.95106 | 0.77051 | 0.48175 | 0.12533 | -0.24869 | -0.58779 | -0.84433 | -0.98229 | -0.98229 | -0.84433 | -0.58779 | -0.24869 | 0.12533 | 0.48175 | 0.77051 | 0.95106 | 0.99803 | 0.90483 | 0.68455 | 0.36812 | -4.9615e-15 | -0.36812 | -0.68455 | -0.90483 | -0.99803 | -0.95106 | -0.77051 | -0.48175 | 0
IDEAL Current
HARMONICS OVERVIEW

## Slide 26
HARMONIC
SOLUTIONS

## Slide 27: HARMONIC MITIGATION OPTIONS
Reactor (AC/DC)
Passive Harmonic Filters
Multi-Pulse Rectifiers
Active Front End (AFE)
All
Yaskawa
Options
HARMONICS SOLUTIONS
Notes: Okay, so your VFDs result harmonics. You have several means to choose from for reducing, or mitigating, harmonics. But you should be aware that all these harmonics mitigation methods, just like medications, have side-effects – they cost money, take up space, and use energy.
[click to bring in graphic]
DC reactors, also known as DC link chokes, are built-in to the larger VFDs. Why not all? For the reasons just stated, they are not included in the smaller, lower horsepower models, because the smaller the drive, the less harmonic current produced. Keep that thought in mind when we discuss IEEE 519.
Whereas the DC link choke is a one-per-VFD technique, passive harmonic filters can be used to reduce harmonics from several devices.
Multi-pulse rectifiers are usually a one-per-device means of reducing harmonics at the expense of added cost, space, and weight. They can be purchased and connected separately or supplied as a package from the VFD manufacturer.
Active front ends employ a second rectifier that acts to cancel harmonics in a way similar to noise cancelling headphones.
Let’s take a look at some comparisons of the different methods for harmonics, power factor, and efficiency.

## Slide 28: 6-PULSE / STANDARD DRIVES
Charges DC Bus: AC > DC
Only Occurs at Peaks of AC Waveform
Result is Non-Linear Current
Input iTHD = 80%+
Goal: Charge the DC Bus
Diode Bridge
HARMONICS SOLUTIONS

## Slide 29: WHERE DID 6-PULSE COME FROM?
Charge DC Bus at AC Peaks
Each Full Cycle
  3 Positive Peaks
  3 Negative Peaks
3 Positive Peaks
3 Negative Peaks
120˚
HARMONICS SOLUTIONS

## Slide 30: VFD WITH INDUCTOR
Two Inductor Connection Types
Inductors Suppress Change
Current Holds Back at Start
Current Will Continue to Flow Once Started
Input iTHD: 30-40%
Standard
w/Reactor
AC Reactor
DC Reactor
HARMONICS SOLUTIONS

## Slide 31: 12-PULSE
Add Transformer
Phase Shift to Voltage
2 Sets of 3-Phase Voltage
Extra Set of Diodes
Conducts Each Set of 3-Phase Power
Input Voltage
Input Current
HARMONICS SOLUTIONS

## Slide 32: WHY 12-PULSE?
6-PULSE
12-PULSE
3 Positive Peaks
3 Negative Peaks
+
120˚
60˚
6 Positive Peaks
6 Negative Peaks
HARMONICS SOLUTIONS

## Slide 33: HARMONIC FILTERS
Shift Power Burden to Filter
Provides Isolation From Source
Constantly Draws Current From Line
Harmonics Between Filter and Drive
Input iTHD: ~5%
Negatives:
  Lower Efficiency
  Not Reliable
  Causes OV Faults
Input Current
HARMONICS SOLUTIONS

## Slide 34: ACTIVE FRONT END (AFE)
Input Switches Constantly ON/OFF
Changes How Drive Sees Voltage
Current Can’t Just Stop
Flows Through Different Phase
Results
Boosted Voltage on Bus
Continuous Current Draw
Input iTHD: ≤ 5%
Input Current
Active Front End
Drive
All-in-One Active Front End
HARMONICS SOLUTIONS

## Slide 35: REDUCING VFD HARMONICS
VFD Harmonics Mitigation
DC Reactor (DC Link Choke)
  Maintains Current Draw
Multi-Pulse Rectifiers
  Draws Current More Often
Active Front End
  Forces Current Draw by Boosting DC bus
All these cost money and reduce efficiency!
Low-Harmonics VFD Design
AC-to-AC Design Creates Sinusoidal Current
HARMONICS SOLUTIONS
Notes: You have several means to choose from for reducing, or mitigating, harmonics. But you should be aware that all these harmonics mitigation methods, just like medications, have side-effects – they cost money, take up space, and use energy.
[click to bring in graphic]
DC reactors, also known as DC link chokes, are built-in to the larger VFDs.
Multi-pulse rectifiers are usually a one-per-device means of reducing harmonics at the expense of added cost, space, and weight. They can be purchased and connected separately or supplied as a package from the VFD manufacturer.
Active front ends employ an additional IGBT section (just like the drive’s output) on the front end of the device. The switches force the dc bus to a higher level allowing current to draw more linearly, thus reducing harmonics. Again, AFE’s provide a benefit at the expense of added cost, space, and weight.
The matrix drive innovative technology changes the way harmonics are mitigated by drawing current naturally as it generates its output.

## Slide 36: REDUCING VFD HARMONICS
VFD Harmonics Mitigation
DC Reactor (DC Link Choke)
  Maintains Current Draw
Multi-pulse Rectifiers
  Draws Current More Often
Active Front End
  Forces Current Draw by Boosting DC Bus
Low-harmonics VFD Design
AC-to-AC Design Creates Sinusoidal Current
All of these
COST MONEY & REDUCE EFFICIENCY
COMPACT SIZE
Notes: You have several means to choose from for reducing, or mitigating, harmonics. But you should be aware that all these harmonics mitigation methods, just like medications, have side-effects – they cost money, take up space, and use energy.
[click to bring in graphic]
DC reactors, also known as DC link chokes, are built-in to the larger VFDs.
Multi-pulse rectifiers are usually a one-per-device means of reducing harmonics at the expense of added cost, space, and weight. They can be purchased and connected separately or supplied as a package from the VFD manufacturer.
Active front ends employ an additional IGBT section (just like the drive’s output) on the front end of the device. The switches force the dc bus to a higher level allowing current to draw more linearly, thus reducing harmonics. Again, AFE’s provide a benefit at the expense of added cost, space, and weight.
The matrix drive innovative technology changes the way harmonics are mitigated by drawing current naturally as it generates its output.

## Slide 37: COMPARISON DETAILS
Variable Frequency Drive without reactor
Variable Frequency Drive with DC reactor
Variable Frequency Drive with multi-pulse
Matrix Variable Frequency Drive
VFD
MATRIX
VFD
VFD
33%
0.90
6 to 12%
0.95
3 to 5%
0.98
Chart: iTHD
| 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25
Distortion | 1 | 0.7 | 0.45 | 0.15 | 0.12 | 0.08 | 0.06 | 0.06 | 0.01
Current Waveform
Current Distortion
True Power Factor
88%
0.75
Current Harmonics
Fundamental Wave
Rated Power Operation
HARMONICS PERFORMANCE
Notes: This is a graphic that gives a good visual representation of the differences in harmonics and power factor for the different mitigation methods.
[read each before clicking to bring in graphic]
On the far left you have the different configurations. Then, we show the breakdown in harmonics. More important is the next three columns. We have an image of the current waveform, its total harmonic distortion and its corresponding power factor.
The goal is to have the input current waveform look like the voltage waveform. In other words the input current waveform should look like a sine wave. As you go from each and eventually reaching the AC to AC matrix drive you will see that the current waveform looks more and more like a sine wave. You will see that the harmonic distortion reduces and power factor increases as you go down the list. As you can see the matrix drive current waveform is nearly sinosoidal, current harmonics are less than 5% and the power factor is 0.98 or better (but never leading).