## Constants (hidden)
Password = yea | [19 empty] | Password = yea | [10 empty] | Password = yea
[19 empty] | End | [6 empty] | End |  |  |  | End | [9 empty] | End
[19 empty] | End | [6 empty] | End |  |  |  | End |  | Consistency Table | [7 empty] | End
| ParameterTable | [17 empty] | End | [6 empty] | End |  |  |  | End |  |  |  |  | 0 to 10V | -10V to +10V | 4 to 20mA | 0 to 20mA |  | End
| Gain & Bias Limits |  |  |  |  | Monitors |  |  | Signal Level |  |  | Gain |  |  | Bias |  |  |  | End |  | InputTypeTable |  |  |  |  | End |  |  |  | End |  | G5 | A1 | G5_A1 | X | X | --- | --- |  | End
|  | Bias Lo | Bias Hi | Gain Lo | Gain Hi | A1 | A2 | A3 | A1 Level | A2 Level | A3 Level | A1 Gain | A2 Gain | A3 Gain | A1 Bias | A2 Bias | A3 Bias |  | End |  | index | units | zero | span |  | End |  | InputList |  | End |  | G5HHP | A1 | G5HHP_A1 | X | X | --- | --- |  | End
| G5 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | U1-17 | H3-01 | H3-08 | H3-04 | H3-02 | H3-10 | H3-06 | H3-03 | H3-11 | H3-07 |  | End |  | 0 to 10V | Volts | 0 | 10 |  | End |  | A1 |  | End |  | F7 | A1 | F7_A1 | X | X | --- | --- |  | End
| G5HHP | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | U1-17 | H3-01 | H3-08 | H3-04 | H3-02 | H3-10 | H3-06 | H3-03 | H3-11 | H3-07 |  | End |  | -10V to +10V | Volts | 0 | 10 |  | End |  | A2 |  | End |  | P7 | A1 | P7_A1 | X | X | --- | --- |  | End
| F7 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | U1-17 | H3-01 | H3-08 | H3-04 | H3-02 | H3-10 | H3-06 | H3-03 | H3-11 | H3-07 |  | End |  | 4 to 20mA | mA | 4 | 16 |  | End |  | A3 |  | End |  | E7 | A1 | E7_A1 | X | X | --- | --- |  | End
| P7 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | --- | H3-01 | H3-08 | --- | H3-02 | H3-10 | --- | H3-03 | H3-11 | --- |  | End |  | 0 to 20mA | mA | 0 | 20 |  | End |  |  |  | End |  | G7 | A1 | G7_A1 | X | X | --- | --- |  | End
| E7 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | --- | H3-01 | H3-08 | --- | H3-02 | H3-10 | --- | H3-03 | H3-11 | --- |  | End | [6 empty] | End | End | End | End | End |  | AC7 | A1 | AC7_A1 | X | X | --- | --- |  | End
| G7 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | U1-17 | H3-01 | H3-08 | H3-04 | H3-02 | H3-10 | H3-06 | H3-03 | H3-11 | H3-07 |  | End | End | End | End | End | End | End | End |  |  |  | End |  | J1000 | A1 | J1000_A1 | X | --- | X | X |  | End
| AC7 | -100% | 100% | 0% | 1000% | U1-15 | U1-16 | U1-17 | H3-01 | H3-08 | H3-04 | H3-02 | H3-10 | H3-06 | H3-03 | H3-11 | H3-07 |  | End | [10 empty] | End |  | V1000 | A1 | V1000_A1 | X | --- | --- | --- |  | End
| J1000 | -999.9% | 999.9% | -999.9% | 999.9% | U1-13 | --- | --- | H3-01 | --- | --- | H3-03 | --- | --- | H3-04 | --- | --- |  | End | [10 empty] | End |  | A1000 | A1 | A1000_A1 | X | X | --- | --- |  | End
| V1000 | -999.9% | 999.9% | -999.9% | 999.9% | U1-13 | U1-14 | --- | H3-01 | H3-09 | --- | H3-03 | H3-11 | --- | H3-04 | H3-12 | --- |  | End | [10 empty] | End |  | G5 | A2 | G5_A2 | X | X | X | --- |  | End
| A1000 | -999.9% | 999.9% | -999.9% | 999.9% | U1-13 | U1-14 | U1-15 | H3-01 | H3-09 | H3-10 | H3-03 | H3-11 | H3-07 | H3-04 | H3-12 | H3-08 |  | End | [10 empty] | End |  | G5HHP | A2 | G5HHP_A2 | X | X | X | --- |  | End
[19 empty] | End | [10 empty] | End |  | F7 | A2 | F7_A2 | X | X | X | --- |  | End
End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | End | [10 empty] | End |  | P7 | A2 | P7_A2 | X | X | X | --- |  | End
[30 empty] | End |  | E7 | A2 | E7_A2 | X | X | X | --- |  | End
[30 empty] | End |  | G7 | A2 | G7_A2 | X | X | X | --- |  | End
[30 empty] | End |  | AC7 | A2 | AC7_A2 | X | X | X | --- |  | End
[30 empty] | End |  | V1000 | A2 | V1000_A2 | X | --- | X | X |  | End
[30 empty] | End |  | A1000 | A2 | A1000_A2 | X | X | X | X |  | End
[30 empty] | End |  | G5 | A3 | G5_A3 | X | X | --- | --- |  | End
[30 empty] | End |  | G5HHP | A3 | G5HHP_A3 | X | X | --- | --- |  | End
[30 empty] | End |  | F7 | A3 | F7_A3 | X | X | --- | --- |  | End
[30 empty] | End |  | G7 | A3 | G7_A3 | X | X | --- | --- |  | End
[30 empty] | End |  | AC7 | A3 | AC7_A3 | X | X | --- | --- |  | End
[30 empty] | End |  | A1000 | A3 | A1000_A3 | X | X | --- | --- |  | End
[30 empty] | End | [9 empty] | End
[30 empty] | End | End | End | End | End | End | End | End | End | End | End

## Entry
Password = yea
Analog Input Calibration Formula -- Provides Gain & Bias Values based on Input - Response Requirements
Use this sheet to calculate Gain & Bias values to match a transducer output1 to Frequency Command or PID feedback requirements.
X1 and X2 are the reading from the analog inputs for two points on the sensor curve in percent of input range.
Y1 and Y2 are the desired output associated with X1 and X2 respectively given in percent of output range.
= Bias = H3-04 for Input A1
= Gain = H3-03 for Input A1
Input Selection |  |  |  | Maximum Frequency (FMax) |  |  |  | Limits of Adjustment | [6 empty] | Analog Input Simple Model
VFD Type | A1000 |  |  | E1-04 | 60 | Hz |  | Limits | Gain | Bias
Input | A1 | [6 empty] | Hi | 999.9% | 999.9% |  | InputZero | 0 | Volts
Input Type | 0 to 10V | [6 empty] | Lo | -999.9% | -999.9% |  | InputSpan | 10 | Volts
Data Entry Schemes | Enter the Values for X & Y in Percent (%) or Natural Units | [7 empty] | Calculation Results Gain & Bias |  | Test Gain and Bias at Point (X,Y)
Both Input & Output | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y)
Expressed in % | Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y) |  | Model (A1 on A1000, V1000, J1000)
A1000 Input A1 | U1-13 | Analog In | % of FMax | Freq | U1-13 | Analog In | % of FMax | Freq | H3-03 | H3-04 | U1-13 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter Percents => | 0% | 0 | 0% | 0 | 100% | 10 | 100% | 60 | 100% | 0% | 50% | 5 | 50% | 30
| ↑↑↑↑ |  | ↑↑↑↑ |  | ↑↑↑↑ |  | ↑↑↑↑ |  | ↑↑↑↑ | ↑↑↑↑ | ↑↑↑↑
| Enter |  | Enter |  | Enter |  | Enter |  | Calculation Results |  | Enter
Both Input & Output | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y)
in Natural Units | Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y) |  | Model (A1 on F7, G7, P7, E7, AC7)
A1000 Input A1 | U1-13 | Analog In | % of FMax | Freq | U1-13 | Analog In | % of FMax | Freq | H3-03 | H3-04 | U1-13 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter V/I In, Hz Out => | 0% | 0 | 0% | 0 | 100% | 10 | 100% | 60 | 100% | 0% | 50% | 5 | 50% | 30
|  | ↑↑↑↑ |  | ↑↑↑↑ |  | ↑↑↑↑ |  | ↑↑↑↑ | ↑↑↑↑ | ↑↑↑↑ |  | ↑↑↑↑
|  | Enter |  | Enter |  | Enter |  | Enter | Calculation Results |  |  | Enter
Input in % | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y)
Output in Hz | Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
A1000 Input A1 | U1-13 | Analog In | % of FMax | Freq | U1-13 | Analog In | % of FMax | Freq | H3-03 | H3-04 | U1-13 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter % In, Hz Out => | 0% | 0 | 0% | 0 | 100% | 10 | 100% | 60 | 100% | 0% | 95.3% | 9.53 | 95.3% | 57.18
| ↑↑↑↑ |  |  | ↑↑↑↑ | ↑↑↑↑ |  |  | ↑↑↑↑ | ↑↑↑↑ | ↑↑↑↑ | ↑↑↑↑
| Enter |  |  | Enter | Enter |  |  | Enter | Calculation Results |  | Enter
Pre-calculated Examples
4_to_20_mA with negative offset | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y) |  |  |  | This uses the 0_to_20_mA input with a 4_to_20_mA transducer, and allows reading values less than 4.0 mA to compensate for 'negative' zero offset. For example, a 3.9_to_19.9_mA input.
| Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
A1000 Input A2 | U1-14 | Analog In | % of FMax | Freq | U1-14 | Analog In | % of FMax | Freq | H3-11 | H3-12 | U1-14 | Analog In | % of FMax | Freq
Range: 0 to 20mA | % | mA | % | Hz | % | mA | % | Hz | % | % | % | mA | % | Hz
Enter Percents => | 20% | 4 | 0% | 0 | 100% | 20 | 100% | 60 | 100% | -25% | 0% | 0 | -25% | -15
Bipolar Speed Control for V1000 | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y) |  |  |  | Allows V1000 which has no negative voltage capability to do bipolar speed control. 5.0 Volts is 0.0 rpm.
| Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
V1000 Input A1 | U1-13 | Analog In | % of FMax | Freq | U1-13 | Analog In | % of FMax | Freq | H3-03 | H3-04 | U1-13 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter V/I In, Hz Out => | 0% | 0 | -100% | -60 | 100% | 10 | 100% | 60 | 100% | -100% | 50% | 5 | 0% | 0
Inverting Transducer Signal | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y) |  |  |  | Reversed transducer example: 20% on input = 100% out 80% on input = 0% out This requires negative gain capability. A1000, V1000, & J1000 support negative gain and bias > 100%.
| Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
A1000 Input A2 | U1-14 | Analog In | % of FMax | Freq | U1-14 | Analog In | % of FMax | Freq | H3-11 | H3-12 | U1-14 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter Percents => | 20% | 2 | 100% | 60 | 80% | 8 | 0% | 0 | -33.33% | 133.3% | 50% | 5 | 50% | 30
Inverting Transducer Signal Does Not Work | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y) |  |  |  | Reversed transducer example: G7, F7, AC7, P7, E7, G5, G5HHP do not support negative gain setting nor bias setting greater than 99.9%. Use '1000 Series for this.
| Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
G7 Input A2 | U1-16 | Analog In | % of FMax | Freq | U1-16 | Analog In | % of FMax | Freq | H3-10 | H3-11 | U1-16 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter Percents => | 20% | 2 | 100% | 60 | 80% | 8 | 0% | 0 | -33.33% | 133.3% | 50% | 5 | 50% | 30
Convert Voltage Input to 4_to_20_mA | Point (X1,Y1) |  |  |  | Point (X2,Y2) |  |  |  | G | B | Point (X,Y) |  |  |  | Convert A3 to a 4_to_20_mA input with a 255Ω resistor and gain and bias settings. 255Ω ¦¦ 20,000Ω = 250Ω. 4 mA * 250Ω = 1.0 Volts = 10% 20 mA * 250Ω = 5.0 Volts = 50%
| Actual Input (X1) |  | Desired Output (Y1) |  | Actual Input (X2) |  | Desired Output (Y2) |  | Gain | Bias | Test Input (X) |  | Predicted Output (Y)
A1000 Input A3 | U1-15 | Analog In | % of FMax | Freq | U1-15 | Analog In | % of FMax | Freq | H3-07 | H3-08 | U1-15 | Analog In | % of FMax | Freq
Range: 0 to 10V | % | Volts | % | Hz | % | Volts | % | Hz | % | % | % | Volts | % | Hz
Enter V/I In, Hz Out => | 10% | 1 | 0% | 0 | 50% | 5 | 100% | 60 | 225% | -25% | 30% | 3 | 50% | 30
X1
X2
Y1
Y2
Input
1 Transducer output must be within the analog input's voltage or current range.
This is a calculation aid intended for Yaskawa associates, representatives, distributors and customers. Any suggestions, comments, corrections -- contact Joe Pottebaum (Industrial Applications) at 414-856-2524 or email joseph_pottebaum@yaskawa.com