## Sheet1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  | A.C. LINE WIRING
Q1E3 CONFIGURED MODEL NO. BASE NUMBER Q1E3XXXX |  | WITH OPTION PC CIRCUIT BREAKER CB1 |  |  |  | STANDARD NON-FUSED INPUT DISCONNECT SWITCH S1
240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B011 | H_ _36020 | 20 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | OT30F3 | 30 | 14 - 4 | 55
| B014 | H_ _36025 | 25
| B021 | H_ _36035 | 35
|  | H_ _36040 | 40 |  |  | OT60F3 | 60 | 14 - 4 | 55
| B027 | H_ _36045 | 45
A028 | B034 | H_ _36050 | 50
| B040 | H_ _36060 | 60
A042 |  | H_ _36070 | 70
| B052 |  |  |  |  | OT100F3 | 100 | 8 - 1/0 | 55
|  | H_ _36080 | 80
A054 | B065 | H_ _36090 | 90
| B077 | H_ _36100 | 100
A068 |  | H_ _36110 | 110
A081 |  | H_ _36125 | 125
| B096 |  |  |  |  | H_ _36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120
A104 | B124 | H_ _36150 | 150
A130 |  | J_ _36200LY | 200 | 4 - 4/0 | 225
| B156 |  |  |  |  | J_ _36000S25 | 250 | 3/0 - 350 kcmil | 225
A154 | B180 | J_ _36225 | 225 | 3/0 - 350 kcmil | 225
A192 |  | M_ _36300 | 300 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
A248 | [5 empty] | L_ _36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
| B240 | M_ _36350 | 350 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
| B302 | M_ _36400 | 400
| B361 | M_ _36500 | 500
| B414 | M_ _36600 | 600 |  |  | L_ _36000S60X | 600
| B477 | M__36700 | 700 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
B515
| B590 | M__36800 | 800 |  |  | P__36000S80 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
TABLE 2 |  | A.C. MOTOR WIRING | [6 empty] | REMOTE EQUIPMENT WIRING
Q1E3 CONFIGURED MODEL NO. BASE NUMBER Q1E3XXXX |  | WITHOUT OPTION PK OR P8 TO STANDARD AC DRIVE | WITH OPTION PK AND WITHOUT OPTION P8 LOAD REACTOR L4 |  |  | WITH OPTION P8 MOTOR TERMINAL BLOCK TB3 |  |  | WITH OPTION SF PANEL MOUNTED FUSE BLOCK FOR REMOTE 115V RECEPTACLE
240V | 480V |  | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B011 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE AC DRIVE TECHNICAL MANUAL USE 75 C COPPER WIRE ONLY | RLW-00140_ | 22 - 10 | 4.5 | LFS13003Z | 14 - 2 | 40 - 50 | 22 - 10 | 25
| B014 |  | RLW-00210_ | 14 - 6 | 16
| B021 |  | RLW-00280_
A028 | B027 |  | RLW-00350_
| B034 |  | RLW-00460_
A042 | B040 |  | RLW-00550_ | 6 - 4 OR 2 - 1/0 | 45 OR 50
| B052 |  | RLW-00650_
A054 |  |  | RLW-00830_
| B065 |  |  |  |  | 1423572 | 14 - 10, 8, OR 6 - 2/0 | 35, 40, OR 120
A068 |  |  | RLW-01040_
A081 | B077
A104 | B096 |  | RLW-01300_ | 2, 1, 1/0, 2/0, OR 3/0, 4/0 | 150, 180, OR 250
| B124 |  | RLW-01600_ |  |  | MPDB67003 | 6 - 350 kcmil | 275
A130 |  |  | RLW-02000_
A154 | B156
A192 | B180 |  | RLW-02500_ | 3/0, 4/0, (250-350) kcmil, OR (400-500) kcmil | 250, 325, OR 375
| B240 |  | RLW-03220_ |  |  | 1453129 | (1-2) x (4 - 350 kcmil) | (1-2) x 275
A248 |  |  | RLW-03220_ | (1-2) x (6 - 350 kcmil) | (1-2) x 375
| B302 |  | RLW-04140_
| B361 |  | RLW-05150_
| B414 |  | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR |  | MPDB69093 | (1-2) x (4 - 500 kcmil) | (1-2) x 500
| B477 |  |  |  |  | MPDB69313
| B515 |  | RLW-07500_
| B590 |  |  |  |  | MPDB69543 | (1-2) x (2 - 600 kcmil) | (1-2) x 600
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE - See Dave P with Questions
[11 empty] | Rev | Description | ECO# | Drawn By | Date
[11 empty] | 02 | CHANGED B240 - B414 TO M FRAME CB | 8204 | R.ROH | 2018-04-04
[11 empty] | 01 | ADDED B477, B515, & B590 VOLTAGE CODES | 8391 | NSL | 2018-01-30
[11 empty] | 00 | INITIAL RELEASE | - | AIM | 2017-03-07
ECO #
DRAWN BY
DATE
DESCRIPTION
CHANGED B240 - B414 TO M FRAME CB
ADDED B477, B515, & B590 VOLTAGE CODES
INITIAL RELEASE
REV.
02
01
00
8204
8391
-
R.ROH
NSL
AIM
04/04/18
01/30/18
03/07/17
REVISIONS
TITLE:
CUSTOMER CONNECTION
Q1E3 CONFIGURED
TYPE 3R
SIZE:
C
PAGE:
1 of 2
REVISION:
02
DRAWING #:
UDE00539
DRAWN BY:
A. MEILAHN
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
A. MEILAHN
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
2/23/17
DATE:
2/27/17
DATE:
DATE:
3/6/17
DATE:
2/23/17

## Sheet2
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 3 |  | EARTH GROUND WIRING |  | NEUTRAL |  | CONTROL WIRING
Q1E3 CONFIGURED MODEL NO. BASE NUMBER Q1E3XXXX |  | GROUND LUG |  | PANEL MOUNTED TERMINAL BLOCK TBN1 |  | A1 TERMINAL BLOCKS TB1-TB4 |  | PANEL MOUNTED TERMINAL BLOCK TB1
240V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B011 | 14 - 2/0 | 120 | 14 - 10, 8, OR 6 - 2/0 | 35, 40, OR 120 | 24 - 16 | 4.4 - 5.3 | 26 - 10 | 5.3 - 7.1
B014
B021
A028 | B027
A042 | B034
B040
A054 | B052
A068 | B065
A081 | B077
A104 | B096
A130 | B124T
A154 | B156 | 6 - 250 kcmil | 275 | 6 - 350 kcmil | 275
A192 | B180
A248 | B240
B302
B361
B414
B477
B515
B590
| T | WITH OPTIONS P4 AND PK, GROUND LUG WIRE SIZE RANGE (AWG) IS 6 - 250 kcmil WITH TIGHTENING TORQUE 275 (LB.-IN).
| T | WITH OPTIONS P4 AND PK, PANEL MOUNTED TEMRINAL BLOCK TBN1 WIRE SIZE RANGE (AWG) IS 6 - 350 kcmil WITH TIGHTENING TORQUE 275 (LB.-IN).
TITLE:
CUSTOMER CONNECTION
Q1E3 CONFIGURED
TYPE 3R
SIZE:
C
PAGE:
2 of 2
REVISION:
02
DRAWING #:
UDE00539
DRAWN BY:
A. MEILAHN
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
A. MEILAHN
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
2/23/17
DATE:
2/27/17
DATE:
DATE:
3/6/17
DATE:
2/23/17