## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
| TABLE 1 |  | A.C. LINE WIRING
| GA800 CONFIGURED MODEL NO. BASE NUMBER G8C5XXXX |  | TO CIRCUIT BREAKER CB1
| 240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| A004 | B002 | H_ _36015SA | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120
| A006 | B003 |  |  | OR | OR
|  | B004 |  |  | 8 | 40
|  | B007 |  |  | OR | OR
| A009 | B011 | H_ _36020SA | 20 | 6 - 4 | 45
|  | B014 | H_ _36025SA | 25 | OR | OR
| A015 |  | H_ _36030SA | 30 | 2 | 50
|  | B021 | H_ _36035SA | 35
| A022 |  | H_ _36040SA | 40
|  | B027 | H_ _36045SA | 45
| A028 |  | H_ _36050SA | 50
|  | B034 | H_ _36060SA | 60
|  | B040 | H_ _36050SA | 50
|  | B052 | H_ _36070SA | 70
A042
|  | B065 | H_ _36080SA | 80
| A054 | B077 | H_ _36100SA | 100
| A068 | B096 | H_ _36125SA | 125
| A080 |  | H_ _36100SA | 100
| A104 | B124 | H_ _36150SA | 150
| A130 |  | J_ _36175SA | 175 | 4 - 4/0 | 225
| A154 | B156 | J_ _36200SA | 200 | 3/0 - 350 kcmil | 225
|  | B180 | J_ _36225SA | 225
| A192 |  | J_ _36250SA | 250
| A248 | B240 | L_ _36400U31XSA | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
| A312 | B302
| A360 | B361 | M_ _ 36450SA | 450 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
|  | B414 | M_ _ 36600SA | 600
|  | B477 | P_ _36080SA | 800
B515
B590
| TABLE 2 |  | BLOWER MOTOR STARTER WIRING
| GA800 CONFIGURED MODEL NO. BASE NUMBER G8C5XXXX |  | WITH OPTION TB, TO OVERLOAD RELAY S10
| 240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| A004 | B515 | LRD15 | 18 - 8 | 15
| A006 | B590
A009
A015
A022
A028
A042
A054
A068
A080
A104
A130
A154
A192
A248
A312
A360
|  | B002 | LRD06 | 18 - 8 | 15
B003
B004
B007
B011
B014
B021
B027
B034
B040
B052
B065
B077
B096
B124
B156
B180
B240
B302
B361
B414
B477
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE
[7 empty] | Rev | Description | ECO# | Drawn By | Date
[7 empty] | 01 | ADDED OPTION TB | 10925 | KAP | 2020-10-28
[7 empty] | 00 | INITIAL RELEASE | - | KAP | 2018-07-26
TITLE:
CUSTOMER CONNECTION
GA800 CONFIGURED
TYPE 12 HD RATING
WITH OPTION PJ
SIZE:
C
PAGE:
1 of 2
REVISION:
01
DRAWING #:
UDE00597
DRAWN BY:
K. PEOPLES
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
K. PEOPLES
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
07/26/18
DATE:
07/26/18
DATE:
DATE:
07/26/18
DATE:
07/26/18
ECO #
DRAWN BY
DATE
DESCRIPTION
ADDED OPTION TB
INITIAL RELEASE
REV.
01
00
10925
-
KAP
KAP
10/28/20
07/26/18
REVISIONS

## PAGE 2
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 3 |  | A.C. MOTOR WIRING |  |  |  | EARTH GROUND WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C5XXXX |  | WITH OPTION PH, TO LOAD REACTOR L4 |  |  | OR, WITHOUT OPTION PH, TO STANDARD AC DRIVE | A.C. LINE GROUND LUG |  | BLOWER MOTOR GROUND LUG
240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) |  | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B002 | RLW-03P40_ | 22 - 10 | 4.5 |  | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50
| B003 | RLW-04P80_
A004 | B004 | RLW-07P60_
| B007 | RLW-00110_
A006 | B011 | RLW-00140_
A009 | B014 | RLW-00210_ | 14 - 6 | 16
A015 |  | RLW-00280_
A022
A028 | B021 | RLW-00350_
B027
| B034 | RLW-00460_
A042 | B040 | RLW-00550_ | 6 - 4 OR 2 - 1/0 | 45 OR 50
B052
A054 | B065 | RLW-00830_
A068 | B077 | RLW-01040_
A080
A104 | B096 | RLW-01300_ | 2 - 1 OR 1/0 - 2/0 OR 3/0 - 4/0 | 150 OR 180 OR 250
A130 | B124 | RLW-01600_ |  |  |  | 14 - 2/0 | 120
A154 | B156 | RLW-02000_
A192 | B180 | RLW-02500_ | 2/0 OR 3/0 - 4/0 OR 250 - 350 OR 400 - 500 | 180 OR 250 OR 325 OR 375 | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR USE 75° C COPPER WIRE ONLY
A248 | B240 | RLW-03220_ | (1-2) x (6 - 350 kcmil) | (1-2) x 375
A312 | B302 | RLW-04140_
A360 | B361 | RLW-05150_ |  |  |  | 6 - 250 | 275
| B414 | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR
B477
| B515 | RLW-07500_
B590
TABLE 4 |  | OPTION PJ |  |  |  | CONTROL WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C5XXXX |  | TO DRIVE A1 |  | OR, TO CDBR A2, A3, A4 |  | TERMINAL BLOCK TB1
240V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
A002 | B001 | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL USE 75° C COPPER WIRE ONLY |  |  |  | 26 - 10 | 5.3 - 7.1
A003 | B002
A004 | B003
A006 | B004
A009 | B007
A015 | B011
A022 | B014
A028 | B021
A042 | B027
A054 | B034
A068 | B040
A080 | B052
A104 | B065
B077
B096
B124
A130 | B156 |  |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE CDBR INSTALLATION MANUAL USE 75° C COPPER WIRE ONLY
A154 | B180
A192 | B240
A248 | B302
A312 | B361
A360 | B414
B477
B515
B590
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE
[10 empty] | Rev | Description | ECO# | Drawn By | Date
[10 empty] | 00 | INITIAL RELEASE | - | KM | 2018-06-14
TITLE:
CUSTOMER CONNECTION
GA800 CONFIGURED
TYPE 12 HD RATING
WITH OPTION PJ
SIZE:
C
PAGE:
2 of 2
REVISION:
01
DRAWING #:
UDE00597
DRAWN BY:
K. PEOPLES
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
K. PEOPLES
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
07/26/18
DATE:
07/26/18
DATE:
DATE:
07/26/18
DATE:
07/26/18